## Sheet1
SR. NO. | PLANT/DEPT | DESIG./NAME | RATING (MVA) | Range | Rating Range | SERIAL NUM | Details ( power transformer/ or distribution transformer ) | DGA Status | Water Content Status | Test Date | Electrical Strength(BDV) | Water Content | Total Acidity Number (Neutralization Value) | Dielectric Dissipation Factor(Tan Delta), at 90˚C | Specific Resistance (Resistivity), at 90˚C | Sediment & Sludge | Interfacial Tension | Flash Point | Density, at 20.0˚C | Hydrogen (H2) | Methane (CH4) | Ethane (C2H6) | Ethylene (C2H4) | Acetylene (C2H2) | Carbon Monoxide (CO) | Carbon Dioxide (CO2) | Propane + Propylene (C3H8+C3H6) | Nitrogen (N2) | Oxygen (O2) | DGA Status | Water Content Status | Year | Month
SR. NO. | 300 MW PP | GT-1 | 200 | 200 | 101 to 200 | 13111-001 | Power Transformer | Normal |  | 30.09.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 13 | 17 | 9 | 62 | 2 | 247 | 1918 | 4 | 40548 | 19840 | Normal |  | 2025 | Sep
1 | 300 MW PP | GT-2 | 200 | 200 | 101 to 200 | 13111-002 | Power Transformer | Normal |  | 07.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 4 | 6 | 2 | 12 | BDL | 63 | 774 | 3 | 27112 | 9152 | Normal |  | 2025 | Jul
2 | 300 MW PP | ST-1 | 20 | 20 | 11 to 20 | AFF-005 | Power Transformer | Normal |  | 07.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 35 | 2 | 1 | 17 | BDL | 76 | 680 | 3 | 32758 | 5238 | Normal |  | 2025 | Jul
3 | 300 MW PP | ST-2 | 20 | 20 | 11 to 20 | AFF-006 | Power Transformer | Normal |  | 07.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 6 | 3 | 3 | 4 | BDL | 240 | 1441 | 4 | 30555 | 8947 | Normal |  | 2025 | Jul
4 | 300 MW PP | UT-1A | 20 | 20 | 11 to 20 | AFF-002 | Power Transformer | Normal |  | 07.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 8 | 4 | 3 | 4 | BDL | 409 | 2090 | 4 | 37277 | 19891 | Normal |  | 2025 | Jul
5 | 300 MW PP | UT-1B | 20 | 20 | 11 to 20 | AFF-003 | Power Transformer | Normal |  | 08.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 7 | 4 | 3 | 3 | BDL | 366 | 1717 | 5 | 38358 | 16743 | Normal |  | 2025 | Jul
6 | 300 MW PP | UT-2A | 20 | 20 | 11 to 20 | AFF-004 | Power Transformer | Normal |  | 08.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 296 | 1546 | 4 | 35712 | 8914 | Normal |  | 2025 | Jul
7 | 300 MW PP | UT-2B | 20 | 20 | 11 to 20 | AFF001 | Power Transformer | Normal |  | 08.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 10 | 4 | 3 | 4 | BDL | 325 | 1795 | 5 | 33197 | 9805 | Normal |  | 2025 | Jul
8 | 300 MW PP | ST-1(OLTC) | 20 | 20 | 11 to 20 | AFF-005 | Power Transformer | Normal |  | 04.07.2025 |  |  | NA | NA | NA | NA | NA | NA | NA | 24 | 4 | 71 | 2 | BDL | 35 | 694 | 3 | 26289 | 7101 | Normal |  | 2025 | Jul
9 | 300 MW PP | ST-2(OLTC) | 20 | 20 | 11 to 20 | AFF006 | Power Transformer | Normal | Normal | 19.04.2025 | 53 | 22 | 0.02 | 0.03 | 635 | Not detected | 36.4 | 164 | 0.842 | 13 | 2 | 3 | 3 | BDL | 133 | 1481 | 4 | 30798 | 18777 | Normal | Normal | 2025 | Apr
10 | 300 MW PP | UT-1A(OLTC) | 20 | 20 | 11 to 20 | AFF-002 | Power Transformer | Normal | Normal | 19.04.2025 | 67 | 34 | 0.02 | 0.001 | 286 | Not detected | 35.6 | 170 | 0.837 | 10 | 2 | 2 | 2 | BDL | 38 | 643 | 3 | 35179 | 17329 | Normal | Normal | 2025 | Apr
11 | 300 MW PP | UT-1B(OLTC) | 20 | 20 | 11 to 20 | AFF-003 | Power Transformer | Normal | Normal | 19.04.2025 | 64 | 20 | 0.02 | 0.0004 | 475 | Not detected | 36 | 170 | 0.837 | 21 | 3 | 3 | 3 | BDL | 36 | 522 | 4 | 37815 | 17619 | Normal | Normal | 2025 | Apr
12 | 300 MW PP | UT-2A(OLTC) | 20 | 20 | 11 to 20 | AFF004 | Power Transformer | Normal | Normal | 21.04.2025 | 70 | 21 | 0.02 | 0.0006 | 1118 | Not detected | 35.9 | 164 | 0.827 | 21 | 2 | 2 | 2 | BDL | 33 | 487 | 4 | 31683 | 16548 | Normal | Normal | 2025 | Apr
13 | 300 MW PP | UT-2B(OLTC) | 20 | 20 | 11 to 20 | AFF001 | Power Transformer | Normal | Normal | 21.04.2025 | 82 | 25 | 0.02 | 0.002 | 1409 | Not detected | 37.3 | 166 | 0.827 | 8 | 3 | 2 | 2 | BDL | 16 | 262 | 3 | 33508 | 13023 | Normal | Normal | 2025 | Apr
14 | 300 MW PP | ESP-1 TR - 1A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/01 | Distribution Transformer | Normal | Moderate | 22.04.2025 | 56 | 60 | 0.02 | 0.0002 | 1917 | Not detected | 41.1 | 164 | 0.962 | 2 | 4 | 4 | 4 | BDL | 23 |  | 7 | 61466 | 28639 | Normal | Moderate | 2025 | Apr
15 | 300 MW PP | ESP-1 TR - 2A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/02 | Distribution Transformer | Normal | Normal | 22.04.2025 | 67 | 32 | 0.02 | 0.0004 | 2195 | Not detected | 42.5 | 166 | 0.962 | 1 | 4 | 4 | 4 | BDL | 24 | 724 | 7 | 62146 | 27230 | Normal | Normal | 2025 | Apr
16 | 300 MW PP | ESP-1 TR - 3A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/03 | Distribution Transformer | Normal | Normal | 22.04.2025 | 62 | 30 | 0.02 | 0.0002 | 3886 | Not detected | 45.4 | 178 | 0.957 | 4 | 8 | 4 | 4 | BDL | 66 | 710 | 7 | 65245 | 22097 | Normal | Normal | 2025 | Apr
17 | 300 MW PP | ESP-1 TR - 4A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/04 | Distribution Transformer | Normal | Normal | 22.04.2025 | 56 | 38 | 0.02 | 0.002 | 4149 | Not detected | 47.1 | 164 | 0.962 | 38 | 38 | 5 | 8 | BDL | 761 | 7414 | 7 | 64256 | 14671 | Normal | Normal | 2025 | Apr
18 | 300 MW PP | ESP-1 TR - 1B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/05 | Distribution Transformer | Normal | Normal | 22.04.2025 | 63 | 36 | 0.02 | 0.0002 | 4238 | Not detected | 47.6 | 166 | 0.962 | 6 | 12 | 4 | 5 | BDL | 143 | 2819 | 7 | 65255 | 24108 | Normal | Normal | 2025 | Apr
19 | 300 MW PP | ESP-1 TR - 2B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/06 | Distribution Transformer | Normal | Moderate | 24.04.2025 | 42 | 44 | 0.02 | 0.0001 | 3665 | Not detected | 46.9 | 178 | 0.962 | 1 | 5 | 4 | 4 | BDL | 23 | 680 | 8 | 49247 | 26818 | Normal | Moderate | 2025 | Apr
20 | 300 MW PP | ESP-1 TR - 3B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/07 | Distribution Transformer | Normal | Moderate | 25.04.2025 | 57 | 59 | 0.02 | 0.0001 | 4313 | Not detected | 46.3 | 178 | 0.962 | 2 | 6 | 4 | 6 | BDL | 45 | 2653 | 7 | 48913 | 24308 | Normal | Moderate | 2025 | Apr
21 | 300 MW PP | ESP-1 TR - 4B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/08 | Distribution Transformer | Normal | Normal | 25.04.2025 | 57 | 34 | 0.02 | 0.0002 | 2412 | Not detected | 49.2 | 166 | 0.962 | 6 | 6 | 1 | 4 | BDL | 29 | 284 | 7 | 65712 | 31058 | Normal | Normal | 2025 | Apr
22 | 300 MW PP | ESP-2 TR - 1A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/09 | Distribution Transformer | Normal | Normal | 29.04.2025 | 52 | 36 | 0.02 | 0.003 | 3585 | Not detected | 48.9 | 178 | 0.962 | 1 | 7 | 3 | 4 | BDL | 82 | 1704 | 7 | 43539 | 23422 | Normal | Normal | 2025 | Apr
23 | 300 MW PP | ESP-2 TR - 2A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/10 | Distribution Transformer | Normal | Normal | 29.04.2025 | 58 | 35 | 0.02 | 0.0003 | 7059 | Not detected | 46.6 | 178 | 0.962 | 6 | 6 | 4 | 4 | BDL | 102 | 1868 | 7 | 41262 | 23738 | Normal | Normal | 2025 | Apr
24 | 300 MW PP | ESP-2 TR - 3A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/11 | Distribution Transformer | Normal | Normal | 29.04.2025 | 55 | 37 | 0.02 | 0.002 | 3265 | Not detected | 38.6 | 176 | 0.962 | 1 | 5 | 4 | 5 | BDL | 36 | 1836 | 7 | 43212 | 25628 | Normal | Normal | 2025 | Apr
25 | 300 MW PP | ESP-2 TR - 4A | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/12 | Distribution Transformer | Normal | Normal | 29.04.2025 | 67 | 33 | 0.02 | 0.0004 | 5048 | Not detected | 48.9 | 174 | 0.962 | 45 | 25 | 3 | 5 | BDL | 565 | 3439 | 7 | 45872 | 19027 | Normal | Normal | 2025 | Apr
26 | 300 MW PP | ESP-2 TR - 1B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/13 | Distribution Transformer | Normal | Normal | 30.04.2025 | 53 | 37 | 0.02 | 0.004 | 4276 | Not detected | 45.9 | 178 | 0.962 | 9 | 9 | 2 | 4 | BDL | 99 | 1503 | 7 | 43958 | 21899 | Normal | Normal | 2025 | Apr
27 | 300 MW PP | ESP-2 TR - 2B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/14 | Distribution Transformer | Normal | Moderate | 30.04.2025 | 50 | 44 | 0.02 | 0.001 | 5964 | Not detected | 45 | 178 | 0.962 | 2 | 5 | 4 | 4 | BDL | 30 | 941 | 7 | 45788 | 26269 | Normal | Moderate | 2025 | Apr
28 | 300 MW PP | ESP-2 TR - 3B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/15 | Distribution Transformer | Normal | Moderate | 30.04.2025 | 62 | 60 | 0.02 | 0.0001 | 4504 | Not detected | 45.9 | 178 | 0.962 | 1 | 5 | 4 | 4 | BDL | 28 | 1017 | 8 | 46601 | 25709 | Normal | Moderate | 2025 | Apr
29 | 300 MW PP | ESP-2 TR - 4B | 0.122 | 0.122 | 0 - 0.9 | 2011/00447/A/I/16 | Distribution Transformer | Normal | Moderate | 30.04.2025 | 55 | 47 | 0.02 | 0.0004 | 6702 | Not detected | 44.8 | 178 | 0.962 | 1 | 6 | 4 | 4 | BDL | 44 | 1456 | 7 | 48853 | 31227 | Normal | Moderate | 2025 | Apr
575 | 300 MW PP | TRANSFORMER YARD | 200 | 200 | 101 to 200 | GT-1 | Power Transformer
576 | 300 MW PP | TRANSFORMER YARD | 200 | 200 | 101 to 200 | GT-2 | Power Transformer
577 | 300 MW PP | TRANSFORMER YARD | 20 | 20 | 11 to 20 | UNIT TRANSFORMER-1A | Power Transformer
578 | 300 MW PP | TRANSFORMER YARD | 20 | 20 | 11 to 20 | UNIT TRANSFORMER-1B | Power Transformer
579 | 300 MW PP | TRANSFORMER YARD | 20 | 20 | 11 to 20 | STATION TRANSFORMER-1 | Power Transformer
580 | 300 MW PP | TRANSFORMER YARD | 20 | 20 | 11 to 20 | UNIT TRANSFORMER-2A | Power Transformer
581 | 300 MW PP | TRANSFORMER YARD | 20 | 20 | 11 to 20 | UNIT TRANSFORMER-2B | Power Transformer
582 | 300 MW PP | TRANSFORMER YARD | 20 | 20 | 11 to 20 | STATION TRANSFORMER-2 | Power Transformer
583 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-11A | Distribution Transformer
584 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-12A | Distribution Transformer
585 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-13A | Distribution Transformer
586 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-14A | Distribution Transformer
587 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-11B | Distribution Transformer
588 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-12B | Distribution Transformer
589 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-13B | Distribution Transformer
590 | 300 MW PP | ESP-1 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-14B | Distribution Transformer
591 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-21A | Distribution Transformer
592 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-22A | Distribution Transformer
593 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-23A | Distribution Transformer
594 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-24A | Distribution Transformer
595 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-21B | Distribution Transformer
596 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-22B | Distribution Transformer
597 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-23B | Distribution Transformer
598 | 300 MW PP | ESP-2 | 0.122 | 0.122 | 0 - 0.9 | ESP TR SET-24B | Distribution Transformer
599 | 300 MW PP | ESP | 0.122 | 0.122 | 0 - 0.9 | SPARE ESP TRAFO | Distribution Transformer
30 | 500 MW CCPP | GTG 1 | 160 | 160 | 101 to 200 | B-29806 | Power Transformer | Normal | Normal | 17.09.2025 | 80 | 7 | 0.02 | 0.0005 | 2708 | Not detected | 40.7 | 162 | 0.822 | 6 | 2 | 5 | 15 | BDL | 635 | 3472 | 5 | 41728 | 19538 | Normal | Normal | 2025 | Sep
31 | 500 MW CCPP | GTG 2 | 160 | 160 | 101 to 200 | B-30006 | Power Transformer | Normal | Normal | 13.09.2025 | 78 | 6 | 0.02 | 0.0009 | 2064 | Not detected | 41.5 | 164 | 0.827 | 2 | 1 | 2 | 6 | BDL | 33 | 600 | 2 | 35645 | 18667 | Normal | Normal | 2025 | Sep
32 | 500 MW CCPP | GTG 3 | 165 | 165 | 101 to 200 | B-30137 | Power Transformer | Normal | Normal | 16.09.2025 | 87 | 7 | 0.02 | 0.001 | 2643 | Not detected | 40.1 | 172 | 0.822 | 7 | 14 | 6 | 20 | BDL | 241 | 4704 | 2 | 41598 | 15379 | Normal | Normal | 2025 | Sep
33 | 500 MW CCPP | STG 1 | 75 | 75 | 51 to 100 | B-29915 | Power Transformer | Normal | Normal | 13.09.2025 | 75 | 6 | 0.02 | 0.0008 | 2787 | Not detected | 40.6 | 166 | 0.822 | 6 | 11 | 3 | 10 | BDL | 637 | 3136 | 4 | 40571 | 16701 | Normal | Normal | 2025 | Sep
34 | 500 MW CCPP | STG 2 | 165 | 165 | 101 to 200 | B-30111 | Power Transformer | Normal | Normal | 11.09.2025 | 65 | 12 | 0.02 | 0.0003 | 1685 | Not detected | 33.2 | 156 | 0.817 | 5 | 47 | 23 | 12 | BDL | 569 | 5082 | 5 | 42524 | 16442 | Normal | Normal | 2025 | Sep
35 | 500 MW CCPP | ST 1 | 16 | 16 | 11 to 20 | B-29800 | Power Transformer | Normal | Normal | 17.09.2025 | 75 | 17 | 0.02 | 0.0002 | 1079 | Not detected | 42.3 | 160 | 0.822 | 4 | 2 | 3 | 8 | BDL | 678 | 3204 | 4 | 42128 | 18520 | Normal | Normal | 2025 | Sep
36 | 500 MW CCPP | ST 2 | 16 | 16 | 11 to 20 | B-29801 | Power Transformer | Normal | Normal | 13.09.2025 | 74 | 5 | 0.02 | 0.001 | 4235 | Not detected | 40 | 162 | 0.822 | 5 | 2 | 2 | 2 | BDL | 249 | 2336 | 4 | 42539 | 26803 | Normal | Normal | 2025 | Sep
37 | 500 MW CCPP | ST 3 (40MVA) | 40 | 40 | 21 to 50 | HT1319/11558 | Power Transformer | Normal | Normal | 13.09.2025 | 69 | 15 | 0.02 | 0.0009 | 693 | Not detected | 39.3 | 162 | 0.822 | 1 | 4 | 1 | 1 | BDL | 211 | 1231 | 2 | 40358 | 20721 | Normal | Normal | 2025 | Sep
38 | 500 MW CCPP | SST 1 | 1 | 1 | 1 to 2 | I-24968201 | Power Transformer | Normal | Normal | 18.09.2025 | 49 | 29 | 0.02 | 0.0004 | 1201 | Not detected | 38.7 | 158 | 0.822 | 5 | 1 | 3 | 4 | BDL | 68 | 959 | 8 | 41838 | 38345 | Normal | Normal | 2025 | Sep
39 | 500 MW CCPP | SST 2 | 2 | 2 | 1 to 2 | TWBO-2042 D 5222 | Power Transformer | Normal | Normal | 18.09.2025 | 46 | 33 | 0.02 | 0.0002 | 2355 | Not detected | 40.8 | 166 | 0.822 | 14 | 3 | 3 | 5 | BDL | 26 | 747 | 6 | 40678 | 35149 | Normal | Normal | 2025 | Sep
40 | 500 MW CCPP | SST 3 | 2 | 2 | 1 to 2 | JN-7977/1 | Power Transformer | Normal | Normal | 18.09.2025 | 78 | 18 | 0.02 | 0.0004 | 2481 | Not detected | 39.9 | 166 | 0.822 | 2 | 1 | 3 | 4 | BDL | 54 | 1574 | 4 | 44545 | 31229 | Normal | Normal | 2025 | Sep
41 | 500 MW CCPP | SST 4 | 2 | 2 | 1 to 2 | 11689/2 | Power Transformer | Normal | Normal | 12.09.2025 | 67 | 18 | 0.02 | 0.0004 | 4905 | Not detected | 41.1 | 168 | 0.827 | 16 | 2 | 3 | 2 | BDL | 249 | 2336 | 4 | 42539 | 26803 | Normal | Normal | 2025 | Sep
42 | 500 MW CCPP | SST 5 | 2 | 2 | 1 to 2 | 11689/1 | Power Transformer | Normal | Normal | 17.09.2025 | 42 | 19 | 0.02 | 0.001 | 2664 | Not detected | 40.7 | 162 | 0.822 | 2 | 2 | 3 | 4 | BDL | 33 | 1281 | 5 | 42456 | 19538 | Normal | Normal | 2025 | Sep
43 | 500 MW CCPP | SST 6 | 2 | 2 | 1 to 2 | 12435/1 | Power Transformer | Normal | Normal | 19.09.2025 | 51 | 21 | 0.02 | 0.0005 | 1514 | Not detected | 34.5 | 162 | 0.822 | 1 | 2 | 4 | 6 | BDL | 51 | 1775 | 5 | 42828 | 30105 | Normal | Normal | 2025 | Sep
44 | 500 MW CCPP | SST 7 | 2 | 2 | 1 to 2 | 12435/2 | Power Transformer | Normal | Normal | 20.09.2025 | 45 | 29 | 0.02 | 0.002 | 262.4 | Not detected | 30.8 | 162 | 0.822 | 1 | 2 | 3 | 4 | BDL | 39 | 776 | 5 | 41523 | 30675 | Normal | Normal | 2025 | Sep
45 | 500 MW CCPP | SST 8 | 2 | 2 | 1 to 2 | 12435/3 | Power Transformer | Normal | Normal | 20.09.2025 | 42 | 30 | 0.02 | 0.0006 | 3004 | Not detected | 39.9 | 166 | 0.822 | 1 | 2 | 3 | 3 | BDL | 38 | 665 | 5 | 40786 | 28975 | Normal | Normal | 2025 | Sep
46 | 500 MW CCPP | SST 9 | 2 | 2 | 1 to 2 | 12435/4 | Power Transformer | Normal | Normal | 11.09.2025 | 70 | 22 | 0.02 | 0.0009 | 1558 | Not detected | 34 | 164 | 0.822 | 1 | 2 | 3 | 3 | BDL | 30 | 643 | 4 | 38420 | 29126 | Normal | Normal | 2025 | Sep
47 | 500 MW CCPP | CWPST 1 | 2 | 2 | 1 to 2 | 11389/2 | Power Transformer | Normal | Normal | 13.09.2025 | 51 | 25 | 0.02 | 0.004 | 1744 | Not detected | 33.7 | 168 | 0.822 | 4 | 2 | 2 | 3 | BDL | 36 | 1219 | 5 | 39322 | 25901 | Normal | Normal | 2025 | Sep
48 | 500 MW CCPP | CWPST 2 | 2 | 2 | 1 to 2 | 11389/1 | Power Transformer | Normal | Normal | 20.09.2025 | 70 | 17 | 0.02 | 0.001 | 2860 | Not detected | 41.3 | 172 | 0.822 | 1 | 2 | 3 | 3 | BDL | 40 | 1386 | 5 | 38765 | 28312 | Normal | Normal | 2025 | Sep
49 | 500 MW CCPP | UAT | 6 | 6 | 6 to 10 | TWB0 - 3177 D7260 | Power Transformer | Normal | Normal | 12.09.2025 | 62 | 9 | 0.02 | 0.001 | 2390 | Not detected | 35.8 | 168 | 0.822 | 1 | 2 | 2 | 4 | BDL | 59 | 1384 | 5 | 40504 | 30758 | Normal | Normal | 2025 | Sep
50 | 500 MW CCPP | GT 1 EXT TR | 0.75 | 0.75 | 0 - 0.9 | NA | Distribution Transformer | Normal | Normal | 12.09.2025 | 51 | 14 | 0.02 | 0.0002 | 2660 | Not detected | 41.3 | 162 | 0.822 | 8 | 2 | 3 | 2 | BDL | 78 | 1128 | 6 | 38134 | 28705 | Normal | Normal | 2025 | Sep
600 | 500MW CCPP | 500MW CCPP | 160 | 160 | 101 to 200 | GTG 1 | Power Transformer
601 | 500MW CCPP | 500MW CCPP | 160 | 160 | 101 to 200 | GTG 2 | Power Transformer
602 | 500MW CCPP | 500MW CCPP | 165 | 165 | 101 to 200 | GTG 3 | Power Transformer
603 | 500MW CCPP | 500MW CCPP | 75 | 75 | 51 to 100 | STG 1 | Power Transformer
604 | 500MW CCPP | 500MW CCPP | 165 | 165 | 101 to 200 | STG 2 | Power Transformer
605 | 500MW CCPP | 500MW CCPP | 16 | 16 | 11 to 20 | ST 1 | Power Transformer
606 | 500MW CCPP | 500MW CCPP | 16 | 16 | 11 to 20 | ST 2 | Power Transformer
607 | 500MW CCPP | 500MW CCPP | 40 | 40 | 21 to 50 | 40MVA | Power Transformer
608 | 500MW CCPP | 500MW CCPP | 1 | 1 | 1 to 2 | SST 1 | Power Transformer
609 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 2 | Power Transformer
610 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 3 | Power Transformer
611 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 4 | Power Transformer
612 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 5 | Power Transformer
613 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 6 | Power Transformer
614 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 7 | Power Transformer
615 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 8 | Power Transformer
616 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | SST 9 | Power Transformer
617 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | CWPST 1 | Power Transformer
618 | 500MW CCPP | 500MW CCPP | 2 | 2 | 1 to 2 | CWPST 2 | Power Transformer
619 | 500MW CCPP | 500MW CCPP | 6 | 6 | 6 to 10 | UAT | Power Transformer
620 | 500MW CCPP | 500MW CCPP | 0.75 | 0.75 | 0 - 0.9 | GT 1 EXT TR | Distribution Transformer
621 | 500MW CCPP | 500MW CCPP | 1 | 1 | 1 to 2 | Spare (SST 1) | Power Transformer
622 | 500MW CCPP | 500MW CCPP | 0.75 | 0.75 | 0 - 0.9 | Spare –(GT 1 EXT TR) | Distribution Transformer
51 | 515 MW PP | GT-1 | 160 | 160 | 101 to 200 | 2007831 | Power Transformer | Normal | Normal | 17.05.2025 | 63 | 7 | NA | NA | NA | NA | NA | NA | NA | 4 | 3 | 3 | 6 | BDL | 305 | 1875 | 4 | 25280 | 10230 | Normal | Normal | 2025 | May
52 | 515 MW PP | GT-2 | 160 | 160 | 101 to 200 | ADT/2007/08 | Power Transformer | Normal | Normal | 17.05.2025 | 61 | 7 | NA | NA | NA | NA | NA | NA | NA | 3 | 12 | 7 | 3 | BDL | 480 | 1782 | 6 | 13814 | 4179 | Normal | Normal | 2025 | May
53 | 515 MW PP | GT-3 | 160 | 160 | 101 to 200 | 16-07-7413 | Power Transformer | Normal | Normal | 17.05.2025 | 67 | 13 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 3 | 6 | BDL | 318 | 2976 | 4 | 17112 | 7364 | Normal | Normal | 2025 | May
54 | 515 MW PP | ST-1 | 16 | 16 | 11 to 20 | T8473/1 | Power Transformer | Normal | Normal | 17.05.2025 | 83 | 8 | NA | NA | NA | NA | NA | NA | NA | 17 | 5 | 20 | 3 | BDL | 139 | 1368 | 12 | 25614 | 11872 | Normal | Normal | 2025 | May
55 | 515 MW PP | ST-2 | 16 | 16 | 11 to 20 | T8473/2 | Power Transformer | Normal | Normal | 17.05.2025 | 63 | 9 | NA | NA | NA | NA | NA | NA | NA | 2 | 20 | 37 | 10 | BDL | 83 | 667 | 16 | 15712 | 6726 | Normal | Normal | 2025 | May
56 | 515 MW PP | STG | 250 | 250 | Above 200 | TWB0-6670/B | Power Transformer | Normal | Normal | 17.05.2025 | 65 | 8 | NA | NA | NA | NA | NA | NA | NA | 4 | 3 | 4 | 10 | BDL | 145 | 1754 | 8 | 29140 | 13859 | Normal | Normal | 2025 | May
57 | 515 MW PP | SST-1 | 2 | 2 | 1 to 2 | 3053/1 | Power Transformer | Normal | Normal | 19.05.2025 | 57 | 34 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 5 | BDL | 41 | 1107 | 7 | 29287 | 14076 | Normal | Normal | 2025 | May
58 | 515 MW PP | SST-2 | 2 | 2 | 1 to 2 | 3053/2 | Power Transformer | Normal | Normal | 19.05.2025 | 45 | 36 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 2 | BDL | 50 | 1516 | 4 | 36981 | 14973 | Normal | Normal | 2025 | May
59 | 515 MW PP | SST-3 | 2 | 2 | 1 to 2 | 41898/1 | Power Transformer | Normal | Normal | 19.05.2025 | 55 | 11 | NA | NA | NA | NA | NA | NA | NA | 17 | 2 | 3 | 4 | BDL | 45 | 1099 | 6 | 33194 | 15304 | Normal | Normal | 2025 | May
60 | 515 MW PP | SST-4 | 2 | 2 | 1 to 2 | 3401/2 | Power Transformer | Normal | Normal | 19.05.2025 | 49 | 25 | NA | NA | NA | NA | NA | NA | NA | 16 | 2 | 3 | 2 | BDL | 41 | 1144 | 4 | 26132 | 11560 | Normal | Normal | 2025 | May
61 | 515 MW PP | SST-5 | 2 | 2 | 1 to 2 | 3401/3 | Power Transformer | Normal | Normal | 19.05.2025 | 52 | 24 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 5 | BDL | 32 | 1444 | 5 | 35633 | 16920 | Normal | Normal | 2025 | May
62 | 515 MW PP | SST-6 | 2 | 2 | 1 to 2 | 4742/1 | Power Transformer | Normal | Normal | 19.05.2025 | 57 | 20 | NA | NA | NA | NA | NA | NA | NA | 3 | 3 | 3 | 6 | BDL | 92 | 1220 | 5 | 29159 | 12246 | Normal | Normal | 2025 | May
63 | 515 MW PP | SST-7 | 2 | 2 | 1 to 2 | 11761/1 | Power Transformer | Normal | Normal | 19.05.2025 | 50 | 14 | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 1 | 1 | BDL | 26 | 970 | 4 | 26758 | 12128 | Normal | Normal | 2025 | May
623 | 515MW PP | 515MW PP | 160 | 160 | 101 to 200 | GT-1 | Power Transformer
624 | 515MW PP | 515MW PP | 160 | 160 | 101 to 200 | GT-2 | Power Transformer
625 | 515MW PP | 515MW PP | 160 | 160 | 101 to 200 | GT-3 | Power Transformer
626 | 515MW PP | 515MW PP | 16 | 16 | 11 to 20 | ST-1 | Power Transformer
627 | 515MW PP | 515MW PP | 16 | 16 | 11 to 20 | ST-2 | Power Transformer
628 | 515MW PP | 515MW PP | 250 | 250 | Above 200 | STG | Power Transformer
629 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-1 | Power Transformer
630 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-2 | Power Transformer
631 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-3 | Power Transformer
632 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-4 | Power Transformer
633 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-5 | Power Transformer
634 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-6 | Power Transformer
635 | 515MW PP | 515MW PP | 2 | 2 | 1 to 2 | SST-7 | Power Transformer
64 | ADMIN | E3 - NN1 | 2 | 2 | 1 to 2 | 3055/17 | Power Transformer | Normal | Moderate | 25.07.2025 | 39 | 47 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 115 | 4861 | 5 | 42175 | 26354 | Normal | Moderate | 2025 | Jul
65 | ADMIN | E3 - NN2 | 2 | 2 | 1 to 2 | 3055/3 | Power Transformer | Normal | Normal | 28.07.2025 | 44 | 31 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 52 | 2584 | 4 | 50068 | 30057 | Normal | Normal | 2025 | Jul
66 | ADMIN | G2 - 10 MVA | 10 | 10 | 6 to 10 | TWBA 2235-05503 | Power Transformer | Normal | Normal | 28.07.2025 | 53 | 17 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 66 | 1478 | 4 | 50168 | 29762 | Normal | Normal | 2025 | Jul
67 | ADMIN | G2 - NN1 | 2 | 2 | 1 to 2 | OCB-004/00 01 | Power Transformer | Normal | Normal | 28.07.2025 | 50 | 23 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 2 | BDL | 11 | 534 | 4 | 76818 | 31537 | Normal | Normal | 2025 | Jul
68 | ADMIN | G2 - NN2 | 3.15 | 3.15 | 3 to 5 | 10 QC 031/01 | Power Transformer | Normal | Normal | 28.07.2025 | 43 | 27 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 3 | BDL | 38 | 938 | 4 | 59087 | 30422 | Normal | Normal | 2025 | Jul
69 | ADMIN | EH- 1 | 2 | 2 | 1 to 2 | JN-11302/1 | Power Transformer | Normal | Normal | 28.07.2025 | 71 | 24 | NA | NA | NA | NA | NA | NA | NA | 4 | 3 | 3 | 4 | BDL | 53 | 1230 | 5 | 42152 | 26351 | Normal | Normal | 2025 | Jul
70 | ADMIN | EH- 2 new | 2 | 2 | 1 to 2 | OC114/01 | Power Transformer | Normal | Normal | 25.07.2025 | 63 | 23 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 41 | 946 | 5 | 41254 | 27957 | Normal | Normal | 2025 | Jul
71 | ADMIN | TR-1 | 2 | 2 | 1 to 2 | PDB 501/0001 | Power Transformer | Normal | Normal | 25.07.2025 | 64 | 15 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 4 | 5 | BDL | 46 | 1098 | 6 | 40142 | 27951 | Normal | Normal | 2025 | Jul
72 | ADMIN | TR-2 | 2 | 2 | 1 to 2 | PDB 501/0002 | Power Transformer | Normal | Normal | 25.07.2025 | 71 | 13 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 4 | 4 | BDL | 35 | 988 | 6 | 41842 | 27052 | Normal | Normal | 2025 | Jul
1188 | ADMIN | AMNS TOWNSHIP | 2 | 2 | 1 to 2 | E3 - NN1 | Power Transformer
1189 | ADMIN | AMNS TOWNSHIP | 2 | 2 | 1 to 2 | E3 - NN2 | Power Transformer
1190 | ADMIN | AMNS TOWNSHIP | 10 | 10 | 6 to 10 | G2 - 10 MVA | Power Transformer
1191 | ADMIN | AMNS TOWNSHIP | 2 | 2 | 1 to 2 | G2 - NN1 | Power Transformer
1192 | ADMIN | AMNS TOWNSHIP | 3.15 | 3.15 | 3 to 5 | G2 - NN2 | Power Transformer
1193 | ADMIN | AMNS TOWNSHIP | 2 | 2 | 1 to 2 | EH- 1 | Power Transformer
1194 | ADMIN | AMNS TOWNSHIP | 2 | 2 | 1 to 2 | EH- 2 new | Power Transformer
1195 | ADMIN | Mora Shanti Park | 2 | 2 | 1 to 2 | TR-1 | Power Transformer
1196 | ADMIN | Mora Shanti Park | 2 | 2 | 1 to 2 | TR-2 | Power Transformer
73 | AMNS Port | ECR-4 DIST. T/F-3 | 2.5 | 2.5 | 3 to 5 | 09 PC-045/03 | Power Transformer | Normal | Normal | 06.09.2025 | 66 | 20 | 0.02 | 0.001 | 706 | Not detected | 40.6 | 178 | 0.837 | 1 | 2 | 3 | 3 | BDL | 30 | 739 | 5 | 38512 | 21709 | Normal | Normal | 2025 | Sep
74 | AMNS Port | Power Trafo-1 | 31.5 | 31.5 | 21 to 50 | 09 2XG 014/02 | Power Transformer | Normal | Normal | 06.09.2025 | 70 | 18 | 0.02 | 0.001 | 268 | Not detected | 42.4 | 178 | 0.827 | 4 | 2 | 3 | 4 | BDL | 275 | 7629 | 4 | 38254 | 22451 | Normal | Normal | 2025 | Sep
75 | AMNS Port | Power Trafo-2 | 31.5 | 31.5 | 21 to 50 | 09 2XG 014/01 | Power Transformer | Normal | Normal | 06.09.2025 | 65 | 9 | 0.02 | 0.002 | 703 | Not detected | 37.2 | 178 | 0.827 | 6 | 2 | 3 | 4 | 2 | 175 | 873 | 4 | 39212 | 24400 | Normal | Normal | 2025 | Sep
76 | AMNS Port | Auxilary Trafo-1 | 2.5 | 2.5 | 3 to 5 | 09 PC-045/04 | Power Transformer | Normal | Normal | 06.09.2025 | 66 | 20 | 0.02 | 0.001 | 706 | Not detected | 40.6 | 178 | 0.837 | 1 | 2 | 3 | 3 | BDL | 30 | 739 | 5 | 38512 | 21709 | Normal | Normal | 2025 | Sep
77 | AMNS Port | Auxilary Trafo-2 | 2.5 | 2.5 | 3 to 5 | 09 PC-045/02 | Power Transformer | Normal | Normal | 06.09.2025 | 68 | 15 | 0.02 | 0.007 | 188 | Not detected | 30.9 | 172 | 0.837 | 7 | 2 | 3 | 5 | BDL | 50 | 1369 | 5 | 38764 | 25478 | Normal | Normal | 2025 | Sep
78 | AMNS Port | Auxilary Trafo-3 | 2 | 2 | 1 to 2 | 050C049/01 | Power Transformer | Normal | Normal | 06.09.2025 | 52 | 32 | 0.02 | 0.003 | 157 | Not detected | 29 | 178 | 0.822 | 36 | 8 | 25 | 10 | BDL | 83 | 2264 | 4 | 38254 | 22451 | Normal | Normal | 2025 | Sep
79 | AMNS Port | Substation Tr-2 | 1 | 1 | 1 to 2 | D5785 | Power Transformer | Moderate |  | 2025-07-03 |  | NA | NA | NA | NA | NA | NA | NA | NA | 92 | 50 | 143 | 214 | BDL | 321 | 3936 | 7 | 43514 | 11204 | Moderate |  | 2025 | Jul
1172 | AMNS PORT | ECR-4 | 12.5/16.5 | 12.5 | 11 to 20 | ECR-4 POWER T/F-1 | Power Transformer
1173 | AMNS PORT | ECR-4 | 12.5/16.5 | 12.5 | 11 to 20 | ECR-4 POWER T/F-2 | Power Transformer
1174 | AMNS PORT | ECR-4 | 2 | 2 | 1 to 2 | ECR-4 DIST. T/F-1 | Power Transformer
1175 | AMNS PORT | ECR-4 | 2 | 2 | 1 to 2 | ECR-4 DIST. T/F-2 | Power Transformer
1176 | AMNS PORT | JETTY LBSS | 2 | 2 | 1 to 2 | LBSS RMHS T/F | Power Transformer
1177 | AMNS PORT | ECR-4 | 2.5 | 2.5 | 3 to 5 | ECR-4 DIST. T/F-3 | Power Transformer
1178 | AMNS PORT | PORTS - LBSS | 31.5 | 31.5 | 21 to 50 | Power Trafo-1 | Power Transformer
1179 | AMNS PORT | PORTS - LBSS | 31.5 | 31.5 | 21 to 50 | Power Trafo-2 | Power Transformer
1180 | AMNS PORT | PORTS - LBSS | 2.5 | 2.5 | 3 to 5 | Auxilary Trafo-1 | Power Transformer
1181 | AMNS PORT | PORTS - LBSS | 2.5 | 2.5 | 3 to 5 | Auxilary Trafo-2 | Power Transformer
1182 | AMNS PORT | BERTH-6 (VADRAJ) | 2 | 2 | 1 to 2 | Auxilary Trafo-3 | Power Transformer
1183 | AMNS PORT | Substation-2 | 2 | 2 | 1 to 2 | Auxilary Trafo-4 | Power Transformer
1184 | AMNS PORT | BOOSTER | 2 | 2 | 1 to 2 | Auxilary Trafo-5 | Power Transformer
1185 | AMNS PORT | ER-2 | 2 | 2 | 1 to 2 | ER-2 TF-1 | Power Transformer
1186 | AMNS PORT | ER-2 | 2 | 2 | 1 to 2 | ER-2 TF-2 | Power Transformer
80 | Blast Furnace | PCM-TRF-1 | 2 | 2 | 1 to 2 | 09 OC -099/01 | Power Transformer | Normal | Normal | 02.09.2025 | 56 | 29 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 4 | BDL | 43 | 1361 | 4 | 42535 | 22681 | Normal | Normal | 2025 | Sep
81 | Blast Furnace | PCI2-TRF-1 | 2 | 2 | 1 to 2 | 09 OC -099/02 | Power Transformer | Normal | Normal | 01.09.2025 | 60 | 14 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 56 | 1795 | 5 | 45141 | 22428 | Normal | Normal | 2025 | Sep
82 | Blast Furnace | PCI2-TRF-2 | 2 | 2 | 1 to 2 | 09 OC -099/04 | Power Transformer | Normal | Normal | 02.09.2025 | 64 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 3 | BDL | 42 | 1307 | 4 | 44708 | 25625 | Normal | Normal | 2025 | Sep
83 | Blast Furnace | PCM-TRF-4 | 2 | 2 | 1 to 2 | 09 OC -099/05 | Power Transformer | Normal | Normal | 02.09.2025 | 56 | 15 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 3 | BDL | 45 | 1140 | 4 | 42955 | 21832 | Normal | Normal | 2025 | Sep
84 | Blast Furnace | PCM-TRF-5 | 2 | 2 | 1 to 2 | 09 OC -099/03 | Power Transformer | Normal | Normal | 02.09.2025 | 47 | 33 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 4 | BDL | 60 | 2033 | 4 | 42763 | 23531 | Normal | Normal | 2025 | Sep
85 | Blast Furnace | CCR-TRF-1 | 2 | 2 | 1 to 2 | 08-OC-094-04 | Power Transformer | Normal | Normal | 30.08.2025 | 62 | 12 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 3 | BDL | 47 | 1452 | 4 | 42454 | 21228 | Normal | Normal | 2025 | Aug
86 | Blast Furnace | CCR-TRF-2 | 2 | 2 | 1 to 2 | 08-OC-094-05 | Power Transformer | Normal | Normal | 30.08.2025 | 71 | 15 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 3 | BDL | 154 | 4384 | 4 | 40945 | 20988 | Normal | Normal | 2025 | Aug
87 | Blast Furnace | CCR-TRF-3 | 1 | 1 | 1 to 2 | 08-LC-079-01 | Power Transformer | Normal | Normal | 30.08.2025 | 57 | 21 | NA | NA | NA | NA | NA | NA | NA | 10 | 2 | 2 | 5 | BDL | 179 | 4897 | 4 | 40233 | 21368 | Normal | Normal | 2025 | Aug
88 | Blast Furnace | CWPS-TRF-1 | 2 | 2 | 1 to 2 | 08-OC-094/06 | Power Transformer | Normal | Normal | 01.09.2025 | 53 | 28 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 4 | BDL | 44 | 1495 | 5 | 42184 | 22320 | Normal | Normal | 2025 | Sep
89 | Blast Furnace | CWPS-TRF-2 | 2 | 2 | 1 to 2 | 08-OC-094/03 | Power Transformer | Normal | Normal | 01.09.2025 | 62 | 20 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 4 | BDL | 42 | 1347 | 4 | 41642 | 23902 | Normal | Normal | 2025 | Sep
90 | Blast Furnace | CWPS-TRF-3 | 2 | 2 | 1 to 2 | 08-OC-094/01 | Power Transformer | Normal | Normal | 01.09.2025 | 66 | 28 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 3 | BDL | 40 | 1391 | 4 | 44383 | 22310 | Normal | Normal | 2025 | Sep
91 | Blast Furnace | CWPS-TRF-4 | 2 | 2 | 1 to 2 | 08-OC-094/02 | Power Transformer | Normal | Normal | 01.09.2025 | 72 | 23 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 34 | 1111 | 5 | 45631 | 22449 | Normal | Normal | 2025 | Sep
92 | Blast Furnace | Venturi-TRF-1 | 1 | 1 | 1 to 2 | 08-LC-080/01 | Power Transformer | Normal | Normal | 01.09.2025 | 48 | 31 | NA | NA | NA | NA | NA | NA | NA | 9 | 3 | 3 | 3 | BDL | 228 | 2312 | 4 | 44618 | 22140 | Normal | Normal | 2025 | Sep
93 | Blast Furnace | Venturi-TRF-2 | 1 | 1 | 1 to 2 | 08-LC-080/02 | Power Transformer | Normal | Normal | 01.09.2025 | 53 | 27 | NA | NA | NA | NA | NA | NA | NA | 14 | 4 | 3 | 5 | BDL | 240 | 2656 | 5 | 44747 | 21957 | Normal | Normal | 2025 | Sep
94 | Blast Furnace | 33kv-TRF-1 | 25 | 25 | 21 to 50 | 07-ZG-011/04 | Power Transformer | Normal | Normal | 30.08.2025 | 63 | 13 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 1 | 4 | BDL | 53 | 1500 | 4 | 41210 | 24861 | Normal | Normal | 2025 | Aug
95 | Blast Furnace | 33kv-TRF-2 | 25 | 25 | 21 to 50 | 07-ZG-011/03 | Power Transformer | Normal | Normal | 30.08.2025 | 67 | 27 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 5 | BDL | 67 | 1554 | 4 | 43427 | 22996 | Normal | Normal | 2025 | Aug
96 | Blast Furnace | CRRS TRF | 2.5 | 2.5 | 3 to 5 | PC 053/01 | Power Transformer | Normal | Normal | 02.09.2025 | 58 | 27 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 5 | BDL | 49 | 1805 | 4 | 44277 | 23865 | Normal | Normal | 2025 | Sep
716 | BLAST FURNACE | PCM | 2 | 2 | 1 to 2 | PCM-TRF-1 | Power Transformer
717 | BLAST FURNACE | PCI-2 | 2 | 2 | 1 to 2 | PCI2-TRF-1 | Power Transformer
718 | BLAST FURNACE | PCI-2 | 2 | 2 | 1 to 2 | PCI2-TRF-2 | Power Transformer
719 | BLAST FURNACE | PCM | 2 | 2 | 1 to 2 | PCM-TRF-4 | Power Transformer
720 | BLAST FURNACE | PCM | 2 | 2 | 1 to 2 | PCM-TRF-5 | Power Transformer
721 | BLAST FURNACE | CCR | 2 | 2 | 1 to 2 | CCR-TRF-1 | Power Transformer
722 | BLAST FURNACE | CCR | 2 | 2 | 1 to 2 | CCR-TRF-2 | Power Transformer
723 | BLAST FURNACE | CCR | 1 | 1 | 1 to 2 | CCR-TRF-3 | Power Transformer
724 | BLAST FURNACE | CWPS | 2 | 2 | 1 to 2 | CWPS-TRF-1 | Power Transformer
725 | BLAST FURNACE | CWPS | 2 | 2 | 1 to 2 | CWPS-TRF-2 | Power Transformer
726 | BLAST FURNACE | CWPS | 2 | 2 | 1 to 2 | CWPS-TRF-3 | Power Transformer
727 | BLAST FURNACE | CWPS | 2 | 2 | 1 to 2 | CWPS-TRF-4 | Power Transformer
728 | BLAST FURNACE | Venturi | 1 | 1 | 1 to 2 | Venturi-TRF-1 | Power Transformer
729 | BLAST FURNACE | Venturi | 1 | 1 | 1 to 2 | Venturi-TRF-2 | Power Transformer
730 | BLAST FURNACE | 33kV SUBSTATION | 25 | 25 | 21 to 50 | 33kv-TRF-1 | Power Transformer
731 | BLAST FURNACE | 33kV SUBSTATION | 25 | 25 | 21 to 50 | 33kv-TRF-2 | Power Transformer
732 | BLAST FURNACE | CRRS | 2.5 | 2.5 | 3 to 5 | CRRS TRF | Power Transformer
1089 | BYPRODUCT | MRP (272 PLOT) | 2 | 2 | 1 to 2 | MRP TRANSFORMER | Power Transformer
1090 | BYPRODUCT | MRP 272 PLOT | 1 | 1 | 1 to 2 | 1 MVA TRAFO | Power Transformer
97 | Corex | 1C911D-T010 | 16/21 | 16 | 11 to 20 | 07YG015/1 | Power Transformer | Normal | Normal | 06.08.2025 | 63 | 21 | 0.02 | 0.002 | 543 | Not detected | 36.5 | 170 | 0.822 | 10 | 2 | 3 | 5 | BDL | 167 | 1951 | 4 | 41676 | 25688 | Normal | Normal | 2025 | Aug
98 | Corex | 2C911D-T010 | 16/21 | 16 | 11 to 20 | 07YG015/4 | Power Transformer | Normal | Normal | 08.08.2025 | 78 | 12 | 0.02 | 0.001 | 2312 | Not detected | 34.5 | 162 | 0.822 | 2 | 2 | 4 | 20 | BDL | 109 | 2237 | 5 | 43398 | 28609 | Normal | Normal | 2025 | Aug
99 | Corex | 1C911D-T020 | 16/21 | 16 | 11 to 20 | 07YG015/3 | Power Transformer | Normal | Normal | 06.08.2025 | 70 | 18 | 0.02 | 0.0006 | 832 | Not detected | 39.4 | 156 | 0.822 | 2 | 2 | 3 | 6 | BDL | 64 | 1633 | 4 | 41400 | 20963 | Normal | Normal | 2025 | Aug
100 | Corex | 2C911D-T020 | 16/21 | 16 | 11 to 20 | 07YG015/2 | Power Transformer | Normal | Normal | 08.08.2025 | 60 | 13 | 0.02 | 0.0005 | 1994 | Not detected | 39.8 | 160 | 0.822 | 1 | 3 | 3 | 3 | BDL | 89 | 3086 | 5 | 41054 | 25385 | Normal | Normal | 2025 | Aug
101 | Corex | 1C911D-T021 | 2 | 2 | 1 to 2 | 07OC064/02 | Power Transformer | Normal | Normal | 06.08.2025 | 74 | 23 | 0.02 | 0.001 | 1352 | Not detected | 39 | 162 | 0.822 | 1 | 2 | 3 | 4 | BDL | 47 | 1962 | 5 | 43341 | 24261 | Normal | Normal | 2025 | Aug
102 | Corex | 1C911D-T022 | 2 | 2 | 1 to 2 | 07OC064/01 | Power Transformer | Normal | Normal | 06.08.2025 | 73 | 25 | 0.02 | 0.004 | 1160 | Not detected | 38 | 170 | 0.822 | 4 | 3 | 2 | 2 | BDL | 48 | 1775 | 4 | 40269 | 21976 | Normal | Normal | 2025 | Aug
103 | Corex | 1C911D-T023 | 2 | 2 | 1 to 2 | 07OC064/04 | Power Transformer | Normal | Normal | 06.08.2025 | 72 | 26 | 0.02 | 0.005 | 1256 | Not detected | 39.5 | 168 | 0.822 | 1 | 2 | 3 | 3 | BDL | 53 | 1715 | 4 | 41856 | 22535 | Normal | Normal | 2025 | Aug
104 | Corex | 1C911D-T024 | 2 | 2 | 1 to 2 | 07OC064/04 | Power Transformer | Normal | Normal | 07.08.2025 | 40 | 38 | 0.02 | 0.064 | 1393 | Not detected | 38.9 | 166 | 0.822 | 1 | 2 | 3 | 3 | BDL | 33 | 813 | 5 | 41876 | 21948 | Normal | Normal | 2025 | Aug
105 | Corex | 1C911D-T024 | 2 | 2 | 1 to 2 | 07OC064/03 | Power Transformer | Normal | Normal | 25.02.2025 | 69 | 20 | NA | NA | NA | NA | NA | NA | NA | 2 | 1 | 1 | 2 | BDL | 22 | 508 | 5 | 41336 | 29704 | Normal | Normal | 2025 | Feb
106 | Corex | 1C911D-T025 | 2.5 | 2.5 | 3 to 5 | 07PC024/2 | Power Transformer | Normal | Normal | 07.08.2025 | 49 | 32 | 0.02 | 0.011 | 1233 | Not detected | 41.1 | 168 | 0.822 | 9 | 2 | 3 | 7 | BDL | 66 | 5582 | 5 | 43170 | 23454 | Normal | Normal | 2025 | Aug
107 | Corex | 1C911D-T026 | 1 | 1 | 1 to 2 | 07LC069/1 | Power Transformer | Normal | Normal | 07.08.2025 | 72 | 15 | 0.02 | 0.003 | 1507 | Not detected | 42.2 | 166 | 0.822 | 2 | 2 | 3 | 3 | BDL | 143 | 2438 | 5 | 40554 | 24734 | Normal | Normal | 2025 | Aug
108 | Corex | 1C911D-T027 | 2.5 | 2.5 | 3 to 5 | 07PC024/3 | Power Transformer | Normal | Normal | 08.08.2025 | 72 | 20 | 0.02 | 0.0004 | 2322 | Not detected | 42.4 | 172 | 0.822 | 1 | 2 | 3 | 3 | BDL | 25 | 1061 | 5 | 41234 | 24518 | Normal | Normal | 2025 | Aug
109 | Corex | 2C911D-T021 | 2 | 2 | 1 to 2 | 07OC064/09 | Power Transformer | Normal | Normal | 08.08.2025 | 58 | 19 | 0.02 | 0.009 | 565 | Not detected | 35.9 | 164 | 0.822 | 3 | 2 | 3 | 3 | BDL | 52 | 1624 | 5 | 41174 | 27895 | Normal | Normal | 2025 | Aug
110 | Corex | 2C911D-T022 | 2 | 2 | 1 to 2 | 07OC064/12 | Power Transformer | Normal | Normal | 09.08.2025 | 73 | 11 | 0.02 | 0.0004 | 1336 | Not detected | 40.6 | 160 | 0.822 | 1 | 2 | 3 | 3 | BDL | 75 | 2225 | 5 | 45431 | 23340 | Normal | Normal | 2025 | Aug
111 | Corex | 2C911D-T023 | 2 | 2 | 1 to 2 | 07OC064/11 | Power Transformer | Normal | Normal | 09.08.2025 | 73 | 17 | 0.02 | 0.006 | 725 | Not detected | 35 | 162 | 0.822 | 1 | 2 | 3 | 3 | BDL | 57 | 1784 | 4 | 41342 | 25309 | Normal | Normal | 2025 | Aug
112 | Corex | 2C911D-T024 | 2 | 2 | 1 to 2 | 07OC064/10 | Power Transformer | Normal | Normal | 09.08.2025 | 41 | 33 | 0.02 | 0.002 | 817 | Not detected | 37.8 | 160 | 0.822 | 1 | 2 | 3 | 3 | BDL | 39 | 1384 | 4 | 45983 | 28247 | Normal | Normal | 2025 | Aug
113 | Corex | 2C911D-T025 | 2.5 | 2.5 | 3 to 5 | 07PC024/1 | Power Transformer | Normal | Normal | 09.08.2025 | 73 | 25 | 0.02 | 0.002 | 974 | Not detected | 38.8 | 164 | 0.822 | 2 | 2 | 3 | 3 | BDL | 38 | 1873 | 4 | 43268 | 28737 | Normal | Normal | 2025 | Aug
114 | Corex | 2C911D-T026 | 1 | 1 | 1 to 2 | 07LC069/2 | Power Transformer | Normal | Normal | 09.08.2025 | 63 | 21 | 0.02 | 0.002 | 543 | Not detected | 36.5 | 170 | 0.822 | 10 | 2 | 3 | 5 | BDL | 167 | 1951 | 4 | 41676 | 25688 | Normal | Normal | 2025 | Aug
733 | COREX | COSA | 16/21 | 16 | 11 to 20 | 1C911D-T010 | Power Transformer
734 | COREX | COSA | 16/21 | 16 | 11 to 20 | 2C911D-T010 | Power Transformer
735 | COREX | COSB | 16/21 | 16 | 11 to 20 | 1C911D-T020 | Power Transformer
736 | COREX | COSB | 16/21 | 16 | 11 to 20 | 2C911D-T020 | Power Transformer
737 | COREX | COSB | 2 | 2 | 1 to 2 | 1C911D-T021 | Power Transformer
738 | COREX | COSB | 2 | 2 | 1 to 2 | 1C911D-T022 | Power Transformer
739 | COREX | COSB | 2 | 2 | 1 to 2 | 1C911D-T023 | Power Transformer
740 | COREX | COSB | 2 | 2 | 1 to 2 | 1C911D-T024 | Power Transformer
741 | COREX | COSB | 2.5 | 2.5 | 3 to 5 | 1C911D-T025 | Power Transformer
742 | COREX | COSB | 1 | 1 | 1 to 2 | 1C911D-T026 | Power Transformer
743 | COREX | COSB | 2.5 | 2.5 | 3 to 5 | 1C911D-T027 | Power Transformer
744 | COREX | COSB | 2 | 2 | 1 to 2 | 2C911D-T021 | Power Transformer
745 | COREX | COSB | 2 | 2 | 1 to 2 | 2C911D-T022 | Power Transformer
746 | COREX | COSB | 2 | 2 | 1 to 2 | 2C911D-T023 | Power Transformer
747 | COREX | COSB | 2 | 2 | 1 to 2 | 2C911D-T024 | Power Transformer
748 | COREX | COSB | 2.5 | 2.5 | 3 to 5 | 2C911D-T025 | Power Transformer
749 | COREX | COSB | 1 | 1 | 1 to 2 | 2C911D-T026 | Power Transformer
115 | CRM | PKL-1 CRM SIDE | 2 | 2 | 1 to 2 | TWBA 1601/D4202 | Power Transformer | Normal | Normal | 30.04.2025 | 56 | 20 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 45 | 922 | 6 | 42133 | 18790 | Normal | Normal | 2025 | Apr
116 | CRM | PKL-1 HSM SIDE | 2 | 2 | 1 to 2 | VF7700/3 | Power Transformer | Normal | Normal | 30.04.2025 | 58 | 23 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 3 | 3 | BDL | 87 | 2653 | 4 | 41852 | 14791 | Normal | Normal | 2025 | Apr
117 | CRM | PKL-2 CRM SIDE | 2 | 2 | 1 to 2 | TWBA 1822/D4990 | Power Transformer | Normal | Normal | 30.04.2025 | 42 | 38 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 3 | 4 | BDL | 75 | 4064 | 5 | 41856 | 13282 | Normal | Normal | 2025 | Apr
118 | CRM | PKL-2 HSM SIDE | 2 | 2 | 1 to 2 | TWBA 1822/D4988 | Power Transformer | Normal | Normal | 30.04.2025 | 54 | 21 | NA | NA | NA | NA | NA | NA | NA | 11 | 4 | 3 | 4 | BDL | 83 | 1895 | 6 | 42154 | 14301 | Normal | Normal | 2025 | Apr
119 | CRM | PKL 3 TR | 2 | 2 | 1 to 2 | 09OC-105 | Power Transformer | Normal | Normal | 03.05.2025 | 54 | 21 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 3 | BDL | 38 | 980 | 5 | 42168 | 11690 | Normal | Normal | 2025 | May
120 | CRM | DRIVE PDB TRAFO | 1 | 1 | 1 to 2 | TWBA - 1870 /05403 | Power Transformer | Normal | Normal | 04.04.2025 | 60 | 21 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 3 | 5 | BDL | 299 | 3992 | 4 | 57263 | 21920 | Normal | Normal | 2025 | Apr
121 | CRM | STD-1 Trafo | 4.6 | 4.6 | 3 to 5 | TWBA - 1869 /D05271 | Power Transformer | Normal | Normal | 02.04.2025 | 53 | 27 | NA | NA | NA | NA | NA | NA | NA | 12 | 2 | 2 | 3 | BDL | 77 | 1304 | 5 | 47021 | 24129 | Normal | Normal | 2025 | Apr
122 | CRM | STD-2 Trafo | 4.6 | 4.6 | 3 to 5 | TWBA - 1869 /D05272 | Power Transformer | Normal | Normal | 02.04.2025 | 59 | 22 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 3 | BDL | 36 | 540 | 5 | 51812 | 21197 | Normal | Normal | 2025 | Apr
123 | CRM | STD-3 Trafo | 4.6 | 4.6 | 3 to 5 | TWBA - 1869 /D05269 | Power Transformer | Normal | Normal | 03.04.2025 | 67 | 23 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 4 | BDL | 88 | 1024 | 5 | 52833 | 20794 | Normal | Normal | 2025 | Apr
124 | CRM | STD-4 Trafo | 5 | 5 | 3 to 5 | D 5270 | Power Transformer | Normal | Normal | 03.04.2025 | 64 | 14 | NA | NA | NA | NA | NA | NA | NA | 13 | 4 | 3 | 3 | BDL | 84 | 858 | 5 | 57025 | 25040 | Normal | Normal | 2025 | Apr
125 | CRM | ACS 800 DRIVE TRAFO | 2 | 2 | 1 to 2 | 1466/1/06 | Power Transformer | Normal | Normal | 03.04.2025 | 66 | 29 | NA | NA | NA | NA | NA | NA | NA | 2 | 6 | 3 | 7 | BDL | 95 | 2873 | 5 | 46877 | 24364 | Normal | Normal | 2025 | Apr
126 | CRM | WELDER TRAFO | 1.6 | 1.6 | 1 to 2 | 145771706 | Power Transformer | Normal | Normal | 03.04.2025 | 54 | 12 | NA | NA | NA | NA | NA | NA | NA | 58 | 6 | 3 | 6 | BDL | 383 | 2127 | 5 | 45154 | 16254 | Normal | Normal | 2025 | Apr
127 | CRM | DISTRIBUTION TRAFO 4 | 2 | 2 | 1 to 2 | TWBA - 1821 /D 4987 | Power Transformer | Normal | Normal | 05.04.2025 | 61 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 73 | 2461 | 5 | 50264 | 24132 | Normal | Normal | 2025 | Apr
128 | CRM | POR BRDL DRV TRAFO | 3 | 3 | 3 to 5 | TWBA - 1697 /D4523 | Power Transformer | Normal | Normal | 03.04.2025 | 55 | 6 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 3 | BDL | 64 | 1067 | 4 | 57937 | 25287 | Normal | Normal | 2025 | Apr
129 | CRM | MILL DRV TRAFO | 5.7 | 5.7 | 6 to 10 | TWBA - 1699 /D4522 | Power Transformer | Normal | Normal | 04.04.2025 | 56 | 18 | NA | NA | NA | NA | NA | NA | NA | 2 | 5 | 3 | 4 | BDL | 76 | 2168 | 7 | 47212 | 25567 | Normal | Normal | 2025 | Apr
130 | CRM | ETR/DTR DRV TRAFO | 4.8 | 4.8 | 3 to 5 | TWBA - 1698 /D4534 | Power Transformer | Normal | Normal | 04.04.2025 | 59 | 16 | NA | NA | NA | NA | NA | NA | NA | 4 | 8 | 4 | 27 | BDL | 125 | 2240 | 8 | 58813 | 25697 | Normal | Normal | 2025 | Apr
131 | CRM | AUX-1 TRAFO | 2 | 2 | 1 to 2 | JN 7201/1 | Power Transformer | Normal | Normal | 04.04.2025 | 57 | 19 | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 3 | 6 | BDL | 66 | 2801 | 6 | 55165 | 24135 | Normal | Normal | 2025 | Apr
132 | CRM | AUX-2 TRAFO | 2 | 2 | 1 to 2 | JN 7201/2 | Power Transformer | Normal | Normal | 04.04.2025 | 63 | 14 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 52 | 2069 | 5 | 44768 | 23112 | Normal | Normal | 2025 | Apr
133 | CRM | CGL-1 TR-1 | 2.25 | 2.25 | 3 to 5 | 7202-2/2026 | Power Transformer | Normal | Normal | 29.04.2025 | 65 | 24 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 2 | BDL | 83 | 3122 | 6 | 35142 | 13822 | Normal | Normal | 2025 | Apr
134 | CRM | CGL-1 TR-2 | 2.25 | 2.25 | 3 to 5 | 7202-1/2026 | Power Transformer | Normal | Normal | 29.04.2025 | 51 | 38 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 61 | 2398 | 6 | 42154 | 14492 | Normal | Normal | 2025 | Apr
135 | CRM | CGL-2 TR-1 | 2 | 2 | 1 to 2 | 1194-1/2026 | Power Transformer | Normal | Normal | 29.04.2025 | 52 | 25 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 2 | BDL | 14 | 572 | 5 | 42154 | 16019 | Normal | Normal | 2025 | Apr
136 | CRM | CGL-2 TR-2 | 2 | 2 | 1 to 2 | 1194-2/2026 | Power Transformer | Normal | Normal | 29.04.2025 | 63 | 13 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 5 | BDL | 79 | 1703 | 5 | 41254 | 17202 | Normal | Normal | 2025 | Apr
137 | CRM | ACTL DISTRIBUTION | 2 | 2 | 1 to 2 | TWBA 1821/D.4984 | Power Transformer | Normal | Normal | 29.04.2025 | 54 | 19 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 6 | BDL | 73 | 2641 | 11 | 41025 | 16327 | Normal | Normal | 2025 | Apr
138 | CRM | H2 PLANT-1 | 1.57 | 1.57 | 1 to 2 | TWBO-3045/D6865 | Power Transformer | Normal | Normal | 22.04.2025 | 52 | 20 | NA | NA | NA | NA | NA | NA | NA | 5 | 3 | 3 | 4 | BDL | 80 | 1897 | 5 | 32168 | 14794 | Normal | Normal | 2025 | Apr
139 | CRM | H2 PLANT-2 | 1.4 | 1.4 | 1 to 2 | 2007-017 | Power Transformer | Normal | Moderate | 22.04.2025 | 41 | 43 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 5 | 9 | BDL | 307 | 6397 | 9 | 35214 | 15755 | Normal | Moderate | 2025 | Apr
140 | CRM | UTILITY Distribution,TR-1 | 2 | 2 | 1 to 2 | 7291/1 | Power Transformer | Normal | Normal | 18.04.2025 | 58 | 9 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 38 | 667 | 7 | 24001 | 9005 | Normal | Normal | 2025 | Apr
141 | CRM | UTILITY Distribution,TR-2 | 2 | 2 | 1 to 2 | 7291/2 | Power Transformer | Normal | Normal | 18.04.2025 | 63 | 11 | NA | NA | NA | NA | NA | NA | NA | 10 | 3 | 3 | 6 | BDL | 51 | 1967 | 5 | 35214 | 11595 | Normal | Normal | 2025 | Apr
142 | CRM | Chiller Distribution TR 1 | 2 | 2 | 1 to 2 | TWBA 1822/D4991 | Power Transformer | Normal | Normal | 17.04.2025 | 47 | 38 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 2 | BDL | 68 | 1478 | 4 | 34816 | 16315 | Normal | Normal | 2025 | Apr
143 | CRM | Chiller Distribution TR 2 | 2 | 2 | 1 to 2 | VF7700/1 | Power Transformer | Normal | Normal | 17.04.2025 | 59 | 16 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 3 | 5 | BDL | 22 | 1542 | 5 | 41856 | 22337 | Normal | Normal | 2025 | Apr
144 | CRM | MSS Distribution, TR-1 | 20 | 20 | 11 to 20 | TWBA 1819/D4938 | Power Transformer | Normal | Normal | 17.04.2025 | 50 | 11 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 3 | BDL | 40 | 1653 | 5 | 39859 | 18500 | Normal | Normal | 2025 | Apr
145 | CRM | CSPM PCC I/C - 2 | 2 | 2 | 1 to 2 | TWBA 1821/D4985 | Power Transformer | Normal | Normal | 09.04.2025 | 49 | 31 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 3 | BDL | 95 | 2834 | 5 | 42546 | 27327 | Normal | Normal | 2025 | Apr
146 | CRM | CSPM PCC I/C - 3 | 2 | 2 | 1 to 2 | TWBA 1821/D4986 | Power Transformer | Normal | Normal | 09.04.2025 | 69 | 17 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 3 | BDL | 69 | 2496 | 5 | 41849 | 26979 | Normal | Normal | 2025 | Apr
147 | CRM | FIMI PCC - I/C -2 TR-1 | 2 | 2 | 1 to 2 | TWBA 2101/D5858 | Power Transformer | Normal | Normal | 10.04.2025 | 55 | 35 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 1 | 2 | BDL | 30 | 1565 | 5 | 43153 | 23104 | Normal | Normal | 2025 | Apr
148 | CRM | FIMI ICTL TR-2 | 2 | 2 | 1 to 2 | TWBA 2101/D5159 | Power Transformer | Normal | Normal | 10.04.2025 | 51 | 31 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 1 | 2 | BDL | 62 | 2477 | 5 | 43158 | 27121 | Normal | Normal | 2025 | Apr
149 | CRM | FIMI ICTL WELDER TR-4 | 2 | 2 | 1 to 2 | 09 OC-106/01 | Power Transformer | Normal | Normal | 10.04.2025 | 54 | 22 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 3 | BDL | 31 | 595 | 5 | 42154 | 22251 | Normal | Normal | 2025 | Apr
150 | CRM | FIMI PCC - I/C -1 TR-3 | 2 | 2 | 1 to 2 | TWBA 1822/D4994 | Power Transformer | Normal | Normal | 10.04.2025 | 47 | 39 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 3 | BDL | 49 | 1232 | 5 | 44121 | 26580 | Normal | Normal | 2025 | Apr
151 | CRM | BAF Distribution, TR1 | 2.5 | 2.5 | 3 to 5 | TWBO 1820/D49660 | Power Transformer | Normal | Normal | 11.04.2025 | 74 | 19 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 3 | BDL | 79 | 3683 | 6 | 41544 | 26508 | Normal | Normal | 2025 | Apr
152 | CRM | BAF Distribution, TR2 | 2.5 | 2.5 | 3 to 5 | TWBO 1820/D49960 | Power Transformer | Normal | Normal | 11.04.2025 | 59 | 17 | NA | NA | NA | NA | NA | NA | NA | 3 | 3 | 4 | 9 | BDL | 62 | 1449 | 10 | 42152 | 23079 | Normal | Normal | 2025 | Apr
153 | CRM | BAF Distribution, TR3 | 2 | 2 | 1 to 2 | TWBA 1822/D4989 | Power Transformer | Normal | Normal | 11.04.2025 | 54 | 23 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 3 | 5 | BDL | 22 | 1542 | 5 | 41856 | 22337 | Normal | Normal | 2025 | Apr
154 | CRM | ECL , TR1 | 2 | 2 | 1 to 2 | TWBA 1822/D4992 | Power Transformer | Normal | Normal | 11.04.2025 | 61 | 31 | NA | NA | NA | NA | NA | NA | NA | 2 | 1 | 2 | 1 | BDL | 59 | 1523 | 5 | 39892 | 19821 | Normal | Normal | 2025 | Apr
155 | CRM | ECL , TR2 | 2 | 2 | 1 to 2 | TWBA 2101/D4993 | Power Transformer | Normal | Normal | 11.04.2025 | 56 | 34 | NA | NA | NA | NA | NA | NA | NA | 21 | 2 | 3 | 4 | BDL | 76 | 1566 | 5 | 44124 | 26112 | Normal | Normal | 2025 | Apr
156 | CRM | ECL , TR3 | 2 | 2 | 1 to 2 | 3863/2 | Power Transformer | Normal | Normal | 11.04.2025 | 46 | 37 | NA | NA | NA | NA | NA | NA | NA | 7 | 2 | 3 | 6 | BDL | 199 | 4218 | 6 | 41512 | 24053 | Normal | Normal | 2025 | Apr
157 | CRM | MSS Lightning ,TR-1 | 0.5 | 0.5 | 0 - 0.9 | TWBA 1823/D5008 | Distribution Transformer | Normal | Normal | 17.04.2025 | 66 | 29 | NA | NA | NA | NA | NA | NA | NA | 10 | 2 | 3 | 5 | BDL | 216 | 3392 | 5 | 42157 | 19666 | Normal | Normal | 2025 | Apr
158 | CRM | MSS Lightning ,TR-2 | 0.5 | 0.5 | 0 - 0.9 | TWBA 1823/D5009 | Distribution Transformer | Normal | Normal | 17.04.2025 | 65 | 25 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 4 | 5 | BDL | 170 | 3080 | 5 | 40240 | 18520 | Normal | Normal | 2025 | Apr
159 | CRM | CSPM TR-4 | 1.25 | 1.25 | 1 to 2 | TWBA 1874 D 5322 | Power Transformer | Moderate | Normal | 09.04.2025 | 72 | 29 | NA | NA | NA | NA | NA | NA | NA | 195 | 2 | 9 | 5 | BDL | 184 | 5282 | 22 | 39272 | 13857 | Moderate | Normal | 2025 | Apr
160 | CRM | CSPM TR-5 | 3.2 | 3.2 | 3 to 5 | TWBA-1872/D5267 | Power Transformer | Normal | Normal | 09.04.2025 | 66 | 9 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 3 | BDL | 66 | 1809 | 7 | 42548 | 28613 | Normal | Normal | 2025 | Apr
161 | CRM | CSPM TR-6 | 3.2 | 3.2 | 3 to 5 | TWBA 1872/D5268 | Power Transformer | Normal | Normal | 09.04.2025 | 57 | 16 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 4 | BDL | 72 | 2150 | 5 | 41541 | 28649 | Normal | Normal | 2025 | Apr
162 | CRM | CSPM TR-7 | 2 | 2 | 1 to 2 | TWBA 1873/D5321 | Power Transformer | Normal | Normal | 09.04.2025 | 69 | 24 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 3 | BDL | 44 | 1393 | 5 | 42154 | 26617 | Normal | Normal | 2025 | Apr
163 | CRM | CSPM TR-8 | 3.2 | 3.2 | 3 to 5 | 4916 | Power Transformer | Normal | Normal | 09.04.2025 | 75 | 8 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 2 | BDL | 48 | 937 | 5 | 43152 | 26329 | Normal | Normal | 2025 | Apr
164 | CRM | PCC - 4 TR-9 | 2 | 2 | 1 to 2 | TWBA 1821/D4987 | Power Transformer | Normal | Normal | 05.04.2025 | 61 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 73 | 2461 | 5 | 50264 | 24132 | Normal | Normal | 2025 | Apr
165 | CRM | PCC - 3 TR-10 | 2 | 2 | 1 to 2 | TWBA 1821/D4980 | Power Transformer | Normal | Normal | 05.04.2025 | 41 | 27 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 54 | 1352 | 6 | 61173 | 29233 | Normal | Normal | 2025 | Apr
166 | CRM | PCC - 2 TR-11 | 2 | 2 | 1 to 2 | TWBA 1821/D4983 | Power Transformer | Normal | Normal | 05.04.2025 | 72 | 13 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 71 | 2835 | 5 | 46168 | 24855 | Normal | Normal | 2025 | Apr
167 | CRM | PCC - 1 TR-12 | 2 | 2 | 1 to 2 | TWBA 1821/D4981 | Power Transformer | Normal | Normal | 05.04.2025 | 66 | 21 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 43 | 1708 | 5 | 46262 | 22796 | Normal | Normal | 2025 | Apr
168 | CRM | ARP-2 TR | 2 | 2 | 1 to 2 | 070C081/01 | Power Transformer | Normal | Normal | 03.05.2025 | 52 | 18 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 12 | 687 | 5 | 41257 | 16762 | Normal | Normal | 2025 | May
169 | CRM | CSPM TR-1 | 2 | 2 | 1 to 2 | D5400 | Power Transformer | Moderate | Normal | 30.04.2024 | 61 | 15 | NA | NA | NA | NA | NA | NA | NA | 122 | 2397 | 1494 | 5126 | 93 | 537 | 4162 | 1890 | 43890 | 30601 | Moderate | Normal | 2024 | Apr
170 | CRM | MSS Distribution, TR-2 | 20 | 20 | 11 to 20 | TWBA-1819-4969 | Power Transformer | Normal | Normal | 25.10.2024 | 53 | 18 | 0.02 | 0.0003 | 1008 | Not detected | 39.5 | 162 | 0.827 | 2 | 2 | 3 | 3 | BDL | 83 | 2674 | 5 | 58887 | 27015 | Normal | Normal | 2024 | Oct
171 | CRM | MDB-1 INC-1 | 2 | 2 | 1 to 2 | 3291/2 | Power Transformer | Normal | Normal | 12.07.2025 | 58 | 38 | 0.02 | 0.127 | 21 | Not detected | 23.1 | 166 | 0.832 | 1 | 3 | 3 | 4 | BDL | 84 | 3181 | 5 | 56120 | 23501 | Normal | Normal | 2025 | Jul
172 | CRM | MDB-1 INC-2 | 2 | 2 | 1 to 2 | 3458/2 | Power Transformer | Normal | Moderate | 12.07.2025 | 59 | 46 | 0.02 | 0.0053 | 32 | Not detected | 22.5 | 160 | 0.827 | 5 | 3 | 5 | 7 | BDL | 117 | 3686 | 4 | 60678 | 24302 | Normal | Moderate | 2025 | Jul
173 | CRM | MDB-2 INC-1 | 2 | 2 | 1 to 2 | 3458/3 | Power Transformer | Normal | Moderate | 12.07.2025 | 58 | 50 | 0.02 | 0.024 | 7 | Not detected | 22.4 | 160 | 0.832 | 2 | 3 | 4 | 6 | BDL | 132 | 3997 | 5 | 65302 | 24568 | Normal | Moderate | 2025 | Jul
174 | CRM | MDB-2 INC-2 | 2 | 2 | 1 to 2 | 3458/4 | Power Transformer | Normal | Normal | 12.07.2025 | 59 | 40 | 0.02 | 0.013 | 13 | Not detected | 22.2 | 164 | 0.852 | 4 | 3 | 3 | 6 | BDL | 105 | 3925 | 5 | 67540 | 23368 | Normal | Normal | 2025 | Jul
175 | CRM | LIGHTING Trafo | 0.5 | 0.5 | 0 - 0.9 | 1839 | Distribution Transformer | Normal | Normal | 14.07.2025 | 66 | 29 | 0.02 | 0.072 | 183 | Not detected | 24.5 | 162 | 0.852 | 24 | 4 | 4 | 6 | BDL | 290 | 4210 | 5 | 80142 | 17818 | Normal | Normal | 2025 | Jul
176 | CRM | SPARE TR | 2 | 2 | 1 to 2 | 3863 | Power Transformer | Normal | Normal | 14.07.2025 | 69 | 35 | 0.02 | 0.008 | 22 | Not detected | 23.5 | 166 | 0.852 | 27 | 3 | 3 | 3 | BDL | 230 | 2311 | 4 | 70905 | 22448 | Normal | Normal | 2025 | Jul
177 | CRM | LBSS-3 | 12.5/16 | 12.5 | 11 to 20 | 4031 | Power Transformer | Normal | Normal | 06.02.2025 | 77 | 23 | NA | NA | NA | NA | NA | NA | NA | 9 | 4 | 3 | 7 | BDL | 320 | 3167 | 5 | 49796 | 22616 | Normal | Normal | 2025 | Feb
178 | CRM | PSL-2 | 2 | 2 | 1 to 2 | 04-OC-44/01 | Power Transformer | Normal | Normal | 06.02.2025 | 72 | 15 | NA | NA | NA | NA | NA | NA | NA | 6 | 3 | 3 | 10 | BDL | 129 | 1231 | 6 | 41523 | 28205 | Normal | Normal | 2025 | Feb
1092 | CRM | LCSS | 1.6 | 1.6 | 1 to 2 | HSPM MILL STAND | Power Transformer
1093 | CRM | LCSS | 1.6 | 1.6 | 1 to 2 | HSPM PAY OFF REE | Power Transformer
1094 | CRM | LCSS | 1.25 | 1.25 | 1 to 2 | HSPM VVVF & AUX. | Power Transformer
1095 | CRM | LCSS | 1.6 | 1.6 | 1 to 2 | TENSION REEL-1 | Power Transformer
1096 | CRM | LCSS | 1.6 | 1.6 | 1 to 2 | TENSION REEL-2 | Power Transformer
1097 | CRM | LCSS | 2 | 2 | 1 to 2 | MDB-1 TR # 1Dist | Power Transformer
1098 | CRM | LCSS | 2 | 2 | 1 to 2 | MDB-1 TR # 2Dist | Power Transformer
1099 | CRM | LCSS | 2 | 2 | 1 to 2 | MDB-2 TR # 1Dist | Power Transformer
1100 | CRM | LCSS | 2 | 2 | 1 to 2 | MDB-2 TR # 2Dist | Power Transformer
1101 | CRM | LCSS | 0.5 | 0.5 | 0 - 0.9 | MLDBLIGHTING | Distribution Transformer
1102 | CRM | LBSS-3 | 12.5 | 12.5 | 11 to 20 | LBSS3 TRAFO | Power Transformer
1103 | CRM | PKL-2 | 2 | 2 | 1 to 2 | Distribution trafo-1 | Power Transformer
1104 | CRM | PKL-2 | 2 | 2 | 1 to 2 | Distribution trafo-2 | Power Transformer
1105 | CRM | PKL-1 | 2 | 2 | 1 to 2 | Distribution trafo-1 | Power Transformer
1106 | CRM | PKL-1 | 2 | 2 | 1 to 2 | Distribution trafo-2 | Power Transformer
1107 | CRM | ARP-1 | 2 | 2 | 1 to 2 | Distribution trafo | Power Transformer
1108 | CRM | PKL-3 | 2 | 2 | 1 to 2 | PKL 3 TR | Power Transformer
1109 | CRM | CTCM | 1 | 1 | 1 to 2 | DRIVE PDB TRAFO | Power Transformer
1110 | CRM | CTCM | 4.6 | 4.6 | 3 to 5 | STD-1 Trafo | Power Transformer
1111 | CRM | CTCM | 4.6 | 4.6 | 3 to 5 | STD-2 Trafo | Power Transformer
1112 | CRM | CTCM | 4.6 | 4.6 | 3 to 5 | STD-3 Trafo | Power Transformer
1113 | CRM | CTCM | 5 | 5 | 3 to 5 | STD-4 Trafo | Power Transformer
1114 | CRM | CTCM | 2 | 2 | 1 to 2 | ACS 800 DRIVE TRAFO | Power Transformer
1115 | CRM | CTCM | 5.25 | 5.25 | 6 to 10 | MV DRIVE TRAFO-1 | Power Transformer
1116 | CRM | CTCM | 5.25 | 5.25 | 6 to 10 | MV DRIVE TRAFO-2 | Power Transformer
1117 | CRM | CTCM | 2 | 2 | 1 to 2 | DISTRIBUTION TRAFO 4 | Power Transformer
1118 | CRM | CTCM | 2 | 2 | 1 to 2 | DISTRIBUTION TRAFO 3 | Power Transformer
1119 | CRM | CTCM | 2 | 2 | 1 to 2 | DISTRIBUTION TRAFO 2 | Power Transformer
1120 | CRM | CTCM | 2 | 2 | 1 to 2 | DISTRIBUTION TRAFO 1 | Power Transformer
1121 | CRM | CTCM | 1.6 | 1.6 | 1 to 2 | WELDER TRAFO | Power Transformer
1122 | CRM | RCM | 3 | 3 | 3 to 5 | POR BRDL DRV TRAFO | Power Transformer
1123 | CRM | RCM | 5.7 | 5.7 | 6 to 10 | MILL DRV TRAFO | Power Transformer
1124 | CRM | RCM | 4.8 | 4.8 | 3 to 5 | ETR/DTR DRV TRAFO | Power Transformer
1125 | CRM | RCM | 2 | 2 | 1 to 2 | AUX-1 TRAFO | Power Transformer
1126 | CRM | RCM | 2 | 2 | 1 to 2 | AUX-2 TRAFO | Power Transformer
1127 | CRM | GAL-1 | 2.25 | 2.25 | 3 to 5 | TR-1 CGL-1 DISTR | Power Transformer
1128 | CRM | GAL-1 | 2.25 | 2.25 | 3 to 5 | TR-2 CGL-1 DISTR | Power Transformer
1129 | CRM | GAL-2 | 2 | 2 | 1 to 2 | TR-1 CGL-2 DISTR | Power Transformer
1130 | CRM | GAL-2 | 2 | 2 | 1 to 2 | TR-2 CGL-2 DISTR | Power Transformer
1131 | CRM | ACTL | 2 | 2 | 1 to 2 | CTL DISTRIBUTION | Power Transformer
1132 | CRM | H2 PLANT-1 | 1.57 | 1.57 | 1 to 2 | H2 PLANT-1 | Power Transformer
1133 | CRM | H2 PLANT-2 | 1.4 | 1.4 | 1 to 2 | H2 PLANT-2 | Power Transformer
1134 | CRM | UTILITY | 2 | 2 | 1 to 2 | UTILITY Distribution,TR-1 | Power Transformer
1135 | CRM | UTILITY | 2 | 2 | 1 to 2 | UTILITY Distribution,TR-2 | Power Transformer
1136 | CRM | CHILLER | 2 | 2 | 1 to 2 | Chiller Distribution TR 1 | Power Transformer
1137 | CRM | CHILLER | 2 | 2 | 1 to 2 | Chiller Distribution TR 2 | Power Transformer
1138 | CRM | MSS | 20 | 20 | 11 to 20 | MSS Distribution, TR-1 | Power Transformer
1139 | CRM | MSS | 20 | 20 | 11 to 20 | MSS Distribution, TR-2 | Power Transformer
1140 | CRM | MSS | 0.5 | 0.5 | 0 - 0.9 | MSS Lightning ,TR-1 | Distribution Transformer
1141 | CRM | MSS | 0.5 | 0.5 | 0 - 0.9 | MSS Lightning, TR-2 | Distribution Transformer
1142 | CRM | CSPM | 2 | 2 | 1 to 2 | PCC I/C - 1 | Power Transformer
1143 | CRM | CSPM | 2 | 2 | 1 to 2 | PCC I/C - 2 | Power Transformer
1144 | CRM | CSPM | 2 | 2 | 1 to 2 | PCC I/C - 3 | Power Transformer
1145 | CRM | CSPM | 1.25 | 1.25 | 1 to 2 | EXT BRD TOP | Power Transformer
1146 | CRM | CSPM | 3.2 | 3.2 | 3 to 5 | MILL TOP & BOTM | Power Transformer
1147 | CRM | CSPM | 3.2 | 3.2 | 3 to 5 | REC A & UNC | Power Transformer
1148 | CRM | CSPM | 2 | 2 | 1 to 2 | ENT BRD, EXT BRD BOT, REC B | Power Transformer
1149 | CRM | CSPM | 3.2 | 3.2 | 3 to 5 | Standby trafo for CSPM TR-5 & 6 | Power Transformer
1150 | CRM | FIMI | 2 | 2 | 1 to 2 | PCC - I/C -1 | Power Transformer
1151 | CRM | FIMI | 2 | 2 | 1 to 2 | PCC - I/C -2 | Power Transformer
1152 | CRM | FIMI | 2 | 2 | 1 to 2 | ICTL | Power Transformer
1153 | CRM | FIMI/ICTL | 2 | 2 | 1 to 2 | ICTL WELDER | Power Transformer
1154 | CRM | BAF | 2.5 | 2.5 | 3 to 5 | Distribution, TR1 | Power Transformer
1155 | CRM | BAF | 2.5 | 2.5 | 3 to 5 | Distribution, TR2 | Power Transformer
1156 | CRM | BAF | 2 | 2 | 1 to 2 | Distribution, TR3 | Power Transformer
1157 | CRM | ECL | 2 | 2 | 1 to 2 | ECL, TR-1 | Power Transformer
1158 | CRM | ECL | 2 | 2 | 1 to 2 | ECL, TR2 | Power Transformer
1159 | CRM | ECL | 2 | 2 | 1 to 2 | ECL, TR3 | Power Transformer
1160 | CRM | LCSS | 2 | 2 | 1 to 2 | HSPM Spare drive | Power Transformer
1161 | CRM | CTCM | 4.8 | 4.8 | 3 to 5 | Spare for Mill stands | Power Transformer
1162 | CRM | CTCM | 5.25 | 5.25 | 6 to 10 | Spare MV Drive Trafo-1 | Power Transformer
1163 | CRM | CTCM | 5.25 | 5.25 | 6 to 10 | Spare MV Drive Trafo-2 | Power Transformer
1164 | CRM | RCM | 2 | 2 | 1 to 2 | Spare for Aux. | Power Transformer
1165 | CRM | RCM | 3 | 3 | 3 to 5 | Spare for POR/BRDL Drive | Power Transformer
1166 | CRM | RCM | 5.7 | 5.7 | 6 to 10 | Spare for Mill Drive | Power Transformer
1167 | CRM | GAL 1&2 SPARE | 2.5 | 2.5 | 3 to 5 | GAL-1&2 DISTRIBUTION | Power Transformer
1170 | CRM | CSPM | 2 | 2 | 1 to 2 | Spare Trafo for CSPM TR 7 | Power Transformer
1171 | CRM | ECL | 1.6 | 1.6 | 1 to 2 | ECL-TR -4 (Spare for Drive) | Power Transformer
179 | CSP Mill | TF trafo-1 | 2.5 | 2.5 | 3 to 5 | 08PC042/01 | Power Transformer | Normal | Normal | 08.05.2025 | 58 | 23 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 38 | 893 | 4 | 41524 | 14087 | Normal | Normal | 2025 | May
180 | CSP Mill | TF trafo-2 | 2.5 | 2.5 | 3 to 5 | 08PC042/02 | Power Transformer | Normal | Normal | 08.05.2025 | 51 | 20 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 45 | 1178 | 5 | 42168 | 14851 | Normal | Normal | 2025 | May
181 | CSP Mill | TF trafo-3 | 2.5 | 2.5 | 3 to 5 | 08PC042/03 | Power Transformer | Normal | Normal | 08.05.2025 | 51 | 28 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 17 | 1003 | 5 | 38664 | 17127 | Normal | Normal | 2025 | May
182 | CSP Mill | Tx.2 for FM1 Drive | 5.1 | 5.1 | 6 to 10 | 1F1422860 | Power Transformer | Normal | Normal | 06.05.2025 | 59 | 13 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 5 | BDL | 106 | 1469 | 5 | 41254 | 16178 | Normal | Normal | 2025 | May
183 | CSP Mill | Tx.3 for FM1 Drive | 5.1 | 5.1 | 6 to 10 | 1LF1422861 | Power Transformer | Normal |  | 2025-09-22 |  | NA | NA | NA | NA | NA | NA | NA | NA | 6 | 28 | 11 | 64 | 3 | 83 | 1398 | 15 | 37038 | 24943 | Normal |  | 2025 | Sep
184 | CSP Mill | Tx.4 for FM2&5 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422804 | Power Transformer | Normal | Normal | 06.05.2025 | 76 | 13 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 6 | BDL | 52 | 787 | 6 | 40760 | 10763 | Normal | Normal | 2025 | May
185 | CSP Mill | Tx.5 for FM2&5 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422805 | Power Transformer | Normal | Normal | 06.05.2025 | 75 | 12 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 57 | 855 | 5 | 41812 | 16528 | Normal | Normal | 2025 | May
186 | CSP Mill | Tx.6 for FM2&5 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422806 | Power Transformer | Normal | Normal | 06.05.2025 | 53 | 12 | NA | NA | NA | NA | NA | NA | NA | 1 | 7 | 5 | 17 | BDL | 57 | 815 | 13 | 38712 | 12639 | Normal | Normal | 2025 | May
187 | CSP Mill | Tx.7 for FM3&6 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422807 | Power Transformer | Normal | Normal | 06.05.2025 | 56 | 8 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 4 | 16 | BDL | 40 | 738 | 10 | 39121 | 11402 | Normal | Normal | 2025 | May
188 | CSP Mill | Tx.8 for FM3&6 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422808 | Power Transformer | Normal | Normal | 07.05.2025 | 59 | 10 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 15 | 227 | 6 | 41922 | 19106 | Normal | Normal | 2025 | May
189 | CSP Mill | Tx.9 for FM3&6 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422809 | Power Transformer | Normal | Normal | 07.05.2025 | 50 | 13 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 3 | BDL | 61 | 892 | 5 | 42944 | 14424 | Normal | Normal | 2025 | May
190 | CSP Mill | Tx.10 for FM4&7 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422810 | Power Transformer | Normal | Normal | 07.05.2025 | 50 | 18 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 7 | BDL | 29 | 491 | 6 | 38664 | 14297 | Normal | Normal | 2025 | May
191 | CSP Mill | Tx.11 for FM4&7 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422811 | Power Transformer | Normal | Normal | 07.05.2025 | 52 | 16 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 4 | BDL | 53 | 557 | 5 | 39654 | 15257 | Normal | Normal | 2025 | May
192 | CSP Mill | Tx.12 for FM4&7 Drive | 7.5 | 7.5 | 6 to 10 | 1F1422812 | Power Transformer | Normal | Normal | 07.05.2025 | 55 | 21 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 3 | BDL | 71 | 989 | 5 | 42154 | 15573 | Normal | Normal | 2025 | May
193 | CSP Mill | Tx.13-Main Trafo | 31.5 | 31.5 | 21 to 50 | 082XG 011/01 | Power Transformer | Normal | Normal | 07.05.2025 | 51 | 17 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 2 | 3 | BDL | 33 | 631 | 5 | 41275 | 16300 | Normal | Normal | 2025 | May
194 | CSP Mill | Tx.14-Main Trafo | 31.5 | 31.5 | 21 to 50 | 082XG 011/02 | Power Transformer | Normal | Normal | 07.05.2025 | 53 | 18 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 41 | 686 | 5 | 42136 | 15515 | Normal | Normal | 2025 | May
195 | CSP Mill | Spare | 5.1 | 5.1 | 6 to 10 | 1LVN2110013859 | Power Transformer | Normal | Normal | 30.11.2024 | 76 | 7 | 0.01 | 0.005 | 1010 | Not detected | 42.7 | 164 | 0.857 | 2 | 2 | 3 | 3 | BDL | 111 | 856 | 4 | 37935 | 24850 | Normal | Normal | 2024 | Nov
196 | CSP Mill | Spare | 5.1 | 5.1 | 6 to 10 | 1LVN2110013858 | Power Transformer | Normal | Normal | 30.11.2024 | 72 | 5 | 0.01 | 0.0002 | 300 | Not detected | 43.5 | 152 | 0.857 | 3 | 2 | 3 | 3 | BDL | 106 | 953 | 4 | 37009 | 24444 | Normal | Normal | 2024 | Nov
197 | CSP Mill | Spare | 7.5 | 7.5 | 6 to 10 | 1LVN2110014063 | Power Transformer | Normal | Normal | 30.11.2024 | 72 | 6 | 0.01 | 0.005 | 830 | Not detected | 40.5 | 162 | 0.857 | 4 | 3 | 3 | 3 | BDL | 175 | 815 | 4 | 38803 | 22248 | Normal | Normal | 2024 | Nov
198 | CSP Mill | Spare | 7.5 | 7.5 | 6 to 10 | 1LVN2110014064 | Power Transformer | Normal | Normal | 30.11.2024 | 71 | 7 | 0.01 | 0.0002 | 1006 | Not detected | 40.2 | 162 | 0.857 | 1 | 2 | 2 | 3 | BDL | 61 | 690 | 4 | 37277 | 25923 | Normal | Normal | 2024 | Nov
199 | CSP Mill | Spare | 7.5 | 7.5 | 6 to 10 | 1LVN2110014065 | Power Transformer | Normal | Normal | 30.11.2024 | 61 | 9 | 0.01 | 0.004 | 836 | Not detected | 40.3 | 156 | 0.857 | 4 | 3 | 3 | 5 | BDL | 122 | 793 | 9 | 38081 | 25539 | Normal | Normal | 2024 | Nov
879 | CSP MILL | Tunnel Furnace trafo bay | 2.5 | 2.5 | 3 to 5 | TF trafo-1 | Power Transformer
880 | CSP MILL | Tunnel Furnace trafo bay | 2.5 | 2.5 | 3 to 5 | TF trafo-2 | Power Transformer
881 | CSP MILL | Tunnel Furnace trafo bay | 2.5 | 2.5 | 3 to 5 | TF trafo-3 | Power Transformer
882 | CSP MILL | Main ECR Trafo bay | 5.1 | 5.1 | 6 to 10 | Tx.2 for FM1 Drive | Power Transformer
883 | CSP MILL | Main ECR Trafo bay | 5.1 | 5.1 | 6 to 10 | Tx.3 for FM1 Drive | Power Transformer
884 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.4 for FM2&5 Drive | Power Transformer
885 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.5 for FM2&5 Drive | Power Transformer
886 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.6 for FM2&5 Drive | Power Transformer
887 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.7 for FM3&6 Drive | Power Transformer
888 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.8 for FM3&6 Drive | Power Transformer
889 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.9 for FM3&6 Drive | Power Transformer
890 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.10 for FM4&7 Drive | Power Transformer
891 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.11 for FM4&7 Drive | Power Transformer
892 | CSP MILL | Main ECR Trafo bay | 7.5 | 7.5 | 6 to 10 | Tx.12 for FM4&7 Drive | Power Transformer
893 | CSP MILL | Main ECR Trafo bay | 31.5 | 31.5 | 21 to 50 | Tx.13-Main Trafo | Power Transformer
894 | CSP MILL | Main ECR Trafo bay | 31.5 | 31.5 | 21 to 50 | Tx.14-Main Trafo | Power Transformer
895 | CSP Mill | Maintenance bay | 5.1 | 5.1 | 6 to 10 | Spare | Power Transformer
897 | CSP Mill | Coil yard | 7.5 | 7.5 | 6 to 10 | Spare | Power Transformer
200 | HBI | T-101 | 20 | 20 | 11 to 20 | 25003 | Power Transformer | Normal | Normal | 19.08.2025 | 68 | 17 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 16 | 5 | BDL | 104 | 951 | 4 | 36472 | 9079 | Normal | Normal | 2025 | Aug
201 | HBI | T-102 | 20 | 20 | 11 to 20 | 25002 | Power Transformer | Normal | Normal | 19.08.2025 | 57 | 21 | NA | NA | NA | NA | NA | NA | NA | 5 | 3 | 13 | 3 | BDL | 163 | 1116 | 4 | 34713 | 9874 | Normal | Normal | 2025 | Aug
202 | HBI | T-103 | 20/25 | 20 | 11 to 20 | R048 | Power Transformer | Normal | Normal | 19.08.2025 | 63 | 20 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 75 | 1501 | 6 | 41549 | 28482 | Normal | Normal | 2025 | Aug
203 | HBI | T-104 | 20/25 | 20 | 11 to 20 | 03 2G-004/0 | Power Transformer | Normal | Normal | 19.08.2025 | 56 | 23 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 3 | BDL | 114 | 2089 | 4 | 40532 | 19581 | Normal | Normal | 2025 | Aug
204 | HBI | 13EE-1 | 2.5 | 2.5 | 3 to 5 | 37763VF | Power Transformer | Normal | Normal | 20.08.2025 | 55 | 23 | NA | NA | NA | NA | NA | NA | NA | 9 | 2 | 2 | 2 | BDL | 187 | 2496 | 4 | 41562 | 21545 | Normal | Normal | 2025 | Aug
205 | HBI | 13EE-2 | 2.5 | 2.5 | 3 to 5 | 37764VF | Power Transformer | Normal | Normal | 20.08.2025 | 55 | 13 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 4 | 4 | BDL | 66 | 1718 | 4 | 41275 | 21608 | Normal | Normal | 2025 | Aug
206 | HBI | 13EE-4 | 2.5 | 2.5 | 3 to 5 | 04PC015/01 | Power Transformer | Normal | Normal | 21.08.2025 | 47 | 32 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 53 | 1512 | 4 | 41741 | 21652 | Normal | Normal | 2025 | Aug
207 | HBI | 13EB-1 | 1.6 | 1.6 | 1 to 2 | 33100 | Power Transformer | Normal | Normal | 19.08.2025 | 43 | 34 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 4 | BDL | 144 | 3689 | 5 | 41518 | 26756 | Normal | Normal | 2025 | Aug
208 | HBI | 13EB-2 | 1.6 | 1.6 | 1 to 2 | 33101 | Power Transformer | Normal | Normal | 19.08.2025 | 54 | 27 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 4 | 5 | BDL | 131 | 2701 | 5 | 42886 | 24721 | Normal | Normal | 2025 | Aug
209 | HBI | 13EB-4 | 2 | 2 | 1 to 2 | 3055/1 | Power Transformer | Normal | Normal | 20.08.2025 | 43 | 40 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 6 | BDL | 143 | 6285 | 5 | 41061 | 19055 | Normal | Normal | 2025 | Aug
210 | HBI | 13ED-1 | 1.6 | 1.6 | 1 to 2 | 34533 | Power Transformer | Normal | Normal | 20.08.2025 | 47 | 32 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 2 | 3 | BDL | 175 | 4857 | 5 | 39613 | 24814 | Normal | Normal | 2025 | Aug
211 | HBI | 13ED-2 | 1.6 | 1.6 | 1 to 2 | 33103 | Power Transformer | Normal | Normal | 20.08.2025 | 56 | 29 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 4 | 6 | BDL | 210 | 3381 | 4 | 41069 | 21877 | Normal | Normal | 2025 | Aug
212 | HBI | 13ED-4 | 2 | 2 | 1 to 2 | 03OC040/01 | Power Transformer | Normal | Normal | 20.08.2025 | 54 | 23 | NA | NA | NA | NA | NA | NA | NA | 9 | 2 | 3 | 7 | BDL | 123 | 1405 | 4 | 39898 | 24073 | Normal | Normal | 2025 | Aug
213 | HBI | 2MVA TRAFO-1 | 2 | 2 | 1 to 2 | 2883 | Power Transformer | Normal | Normal | 21.08.2025 | 43 | 37 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 12 | BDL | 161 | 3367 | 4 | 40275 | 22785 | Normal | Normal | 2025 | Aug
214 | HBI | 2MVA TRAFO-2 | 2 | 2 | 1 to 2 | 04OC045/1 | Power Transformer | Normal | Normal | 21.08.2025 | 48 | 36 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 3 | 4 | BDL | 111 | 1475 | 4 | 42454 | 21695 | Normal | Normal | 2025 | Aug
215 | HBI | 9E7-153 | 1.6 | 1.6 | 1 to 2 | NA | Power Transformer | Normal | Normal | 21.08.2025 | 53 | 22 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 2 | BDL | 122 | 2832 | 5 | 41841 | 21937 | Normal | Normal | 2025 | Aug
216 | HBI | 9E7-154 | 1.6 | 1.6 | 1 to 2 | 33104 | Power Transformer | Normal | Normal | 21.08.2025 | 57 | 27 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 5 | BDL | 133 | 4125 | 4 | 41377 | 20679 | Normal | Normal | 2025 | Aug
217 | HBI | 9E7-155 | 1.6 | 1.6 | 1 to 2 | 33105 | Power Transformer | Normal | Normal | 22.08.2025 | 49 | 33 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 139 | 2598 | 5 | 40575 | 21587 | Normal | Normal | 2025 | Aug
218 | HBI | 9E7-165 | 1.6 | 1.6 | 1 to 2 | 33099 | Power Transformer | Normal | Normal | 22.08.2025 | 45 | 30 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 3 | 4 | BDL | 126 | 2766 | 4 | 42278 | 23638 | Normal | Normal | 2025 | Aug
219 | HBI | 9E7-163 | 1.6 | 1.6 | 1 to 2 | 13102 | Power Transformer | Normal | Normal | 22.08.2025 | 42 | 31 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 3 | 4 | BDL | 135 | 3770 | 4 | 41642 | 23902 | Normal | Normal | 2025 | Aug
220 | HBI | S-S-91/1 | 0.63 | 0.63 | 0 - 0.9 | 37614V | Distribution Transformer | Normal | Normal | 28.08.2023 | 50 | 36 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 3 | BDL | 19 | 1321 | 4 | 45575 | 15395 | Normal | Normal | 2023 | Aug
221 | HBI | AU. SCR.HS | 1.6 | 1.6 | 1 to 2 | 2923 | Power Transformer | Normal | Normal | 21.08.2025 | 50 | 26 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 2 | BDL | 45 | 1305 | 5 | 41346 | 21802 | Normal | Normal | 2025 | Aug
222 | HBI | QM-2 | 35 | 35 | 21 to 50 | 05 2XG-004/02 | Power Transformer | Normal | Normal | 06.07.2025 | 71 | 21 | 0.02 | 0.003 | 304 | Not detected | 35.9 | 170 | 0.827 | 6 | 4 | 2 | 6 | BDL | 101 | 2081 | 5 | 51255 | 22607 | Normal | Normal | 2025 | Jul
223 | HBI | QM-C | 35 | 35 | 21 to 50 | 05 2XG-004/01 | Power Transformer | Normal | Normal | 07.07.2025 | 50 | 29 | 0.02 | 0.0006 | 174 | Not detected | 35.2 | 172 | 0.817 | 4 | 4 | 2 | 2 | BDL | 134 | 3472 | 5 | 44510 | 25311 | Normal | Normal | 2025 | Jul
224 | HBI | T-161 | 40/50 | 40 | 21 to 50 | 07 2ZG 001/01 | Power Transformer | Normal | Normal | 05.07.2025 | 46 | 30 | 0.02 | 0.0005 | 780 | Not detected | 34.8 | 160 | 0.822 | 2 | 4 | 3 | 7 | BDL | 82 | 4373 | 5 | 53521 | 28430 | Normal | Normal | 2025 | Jul
225 | HBI | T-162 | 40/50 | 40 | 21 to 50 | 07 2ZG 001/02 | Power Transformer | Normal | Normal | 05.07.2025 | 75 | 15 | 0.02 | 0.002 | 217 | Not detected | 33.5 | 172 | 0.822 | 1 | 4 | 3 | 7 | BDL | 108 | 3266 | 5 | 45632 | 26403 | Normal | Normal | 2025 | Jul
226 | HBI | EB2 | 2 | 2 | 1 to 2 | 05 OC 048/08 | Power Transformer | Normal | Normal | 07.07.2025 | 73 | 14 | 0.02 | 0.001 | 776 | Not detected | 38.5 | 170 | 0.832 | 14 | 3 | 2 | 2 | BDL | 137 | 1486 | 4 | 36320 | 20408 | Normal | Normal | 2025 | Jul
227 | HBI | ED2 | 2 | 2 | 1 to 2 | 05 OC 048/02 | Power Transformer | Normal | Normal | 07.07.2025 | 67 | 30 | 0.02 | 0.001 | 776 | Not detected | 36 | 170 | 0.822 | 8 | 3 | 1 | 1 | BDL | 139 | 1425 | 4 | 40452 | 23506 | Normal | Normal | 2025 | Jul
228 | HBI | EH2 | 2 | 2 | 1 to 2 | 05 OC 048/04 | Power Transformer | Normal | Normal | 09.07.2025 | 55 | 28 | 0.02 | 0.0004 | 738 | Not detected | 32.7 | 170 | 0.817 | 8 | 3 | 2 | 5 | BDL | 177 | 2232 | 5 | 43335 | 22824 | Normal | Normal | 2025 | Jul
229 | HBI | EL2 | 2 | 2 | 1 to 2 | 05 OC 048/01 | Power Transformer | Normal | Normal | 09.07.2025 | 62 | 26 | 0.02 | 0.001 | 350 | Not detected | 34.7 | 170 | 0.822 | 8 | 3 | 3 | 8 | BDL | 160 | 1970 | 5 | 45964 | 23467 | Normal | Normal | 2025 | Jul
230 | HBI | EE2 | 3 | 3 | 3 to 5 | 05 QC 010/02 | Power Transformer | Normal | Normal | 07.07.2025 | 80 | 24 | 0.02 | 0.0008 | 1201 | Not detected | 33.5 | 168 | 0.822 | 4 | 3 | 2 | 3 | BDL | 46 | 1348 | 4 | 40283 | 25620 | Normal | Normal | 2025 | Jul
231 | HBI | EE-C | 3 | 3 | 3 to 5 | 05 QC 010/01 | Power Transformer | Normal | Normal | 09.07.2025 | 74 | 28 | 0.02 | 0.003 | 122 | Not detected | 33.3 | 168 | 0.817 | 14 | 3 | 1 | 1 | BDL | 55 | 1586 | 5 | 44402 | 23572 | Normal | Normal | 2025 | Jul
232 | HBI | VPSA | 2 | 2 | 1 to 2 | 07 OC 073/01 | Power Transformer | Normal | Normal | 09.07.2025 | 63 | 28 | 0.02 | 0.003 | 201 | Not detected | 34.1 | 170 | 0.822 | 1 | 3 | 3 | 4 | BDL | 37 | 951 | 5 | 43709 | 24821 | Normal | Normal | 2025 | Jul
233 | HBI | T-261 | 3 | 3 | 3 to 5 | 07 QC 019/02 | Power Transformer | Normal | Normal | 05.07.2025 | 71 | 20 | 0.02 | 0.007 | 153 | Not detected | 34.7 | 170 | 0.822 | 1 | 3 | 1 | 3 | BDL | 78 | 3335 | 5 | 48511 | 26605 | Normal | Normal | 2025 | Jul
234 | HBI | T-262 | 3 | 3 | 3 to 5 | 07 QC 019/03 | Power Transformer | Normal | Normal | 05.07.2025 | 68 | 30 | 0.02 | 0.06 | 18.61 | Not detected | 36 | 170 | 0.822 | 2 | 3 | 1 | 3 | BDL | 71 | 2320 | 5 | 38462 | 24510 | Normal | Normal | 2025 | Jul
235 | HBI | T-263 | 3 | 3 | 3 to 5 | 07 QC 019/01 | Power Transformer | Normal | Normal | 06.07.2025 | 66 | 21 | 0.02 | 0.002 | 555 | Not detected | 33.5 | 176 | 0.822 | 3 | 5 | 3 | 6 | BDL | 52 | 1799 | 5 | 36420 | 23110 | Normal | Normal | 2025 | Jul
236 | HBI | T-264 | 1 | 1 | 1 to 2 | 07 LC 071 | Power Transformer | Normal | Normal | 06.07.2025 | 82 | 14 | 0.02 | 0.002 | 436 | Not detected | 33.7 | 172 | 0.822 | 9 | 4 | 2 | 3 | BDL | 207 | 2009 | 4 | 43826 | 24339 | Normal | Normal | 2025 | Jul
750 | HBI | HBI PLANT-A | 20 | 20 | 11 to 20 | T-101 | Power Transformer
751 | HBI | HBI PLANT-A | 20 | 20 | 11 to 20 | T-102 | Power Transformer
752 | HBI | HBI PLANT-A | 20/25 | 20 | 11 to 20 | T-103 | Power Transformer
753 | HBI | HBI PLANT-A | 20/25 | 20 | 11 to 20 | T-104 | Power Transformer
754 | HBI | HBI PLANT-A | 2.5 | 2.5 | 3 to 5 | 13EE-1 | Power Transformer
755 | HBI | HBI PLANT-A | 2.5 | 2.5 | 3 to 5 | 13EE-2 | Power Transformer
756 | HBI | HBI PLANT-A | 2.5 | 2.5 | 3 to 5 | 13EE-4 | Power Transformer
757 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 13EB-1 | Power Transformer
758 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 13EB-2 | Power Transformer
759 | HBI | HBI PLANT-A | 2 | 2 | 1 to 2 | 13EB-4 | Power Transformer
760 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 13ED-1 | Power Transformer
761 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 13ED-2 | Power Transformer
762 | HBI | HBI PLANT-A | 2 | 2 | 1 to 2 | 13ED-4 | Power Transformer
763 | HBI | HBI PLANT-A | 2 | 2 | 1 to 2 | 2MVA TRAFO-1 | Power Transformer
764 | HBI | HBI PLANT-A | 2 | 2 | 1 to 2 | 2MVA TRAFO-2 | Power Transformer
765 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 9E7-153 | Power Transformer
766 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 9E7-154 | Power Transformer
767 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 9E7-155 | Power Transformer
768 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 9E7-165 | Power Transformer
769 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | 9E7-163 | Power Transformer
770 | HBI | HBI PLANT-A | 0.63 | 0.63 | 0 - 0.9 | S-S-91/1 | Distribution Transformer
771 | HBI | HBI PLANT-A | 1.6 | 1.6 | 1 to 2 | AU. SCR.HS | Power Transformer
772 | HBI | HBI PLANT-A | 1.25 | 1.25 | 1 to 2 | FWPH TRAFO-1 | Power Transformer
773 | HBI | HBI PLANT-A | 1.25 | 1.25 | 1 to 2 | FWPH TRAFO-2 | Power Transformer
774 | HBI | HBI PLANT-B | 35 | 35 | 21 to 50 | QM-2 | Power Transformer
775 | HBI | HBI PLANT-B | 35 | 35 | 21 to 50 | QM-C | Power Transformer
776 | HBI | HBI PLANT-B | 40/50 | 40 | 21 to 50 | T-161 | Power Transformer
777 | HBI | HBI PLANT-B | 40/50 | 40 | 21 to 50 | T-162 | Power Transformer
778 | HBI | HBI PLANT-B | 2 | 2 | 1 to 2 | EB2 | Power Transformer
779 | HBI | HBI PLANT-B | 2 | 2 | 1 to 2 | ED2 | Power Transformer
780 | HBI | HBI PLANT-B | 2 | 2 | 1 to 2 | EH2 | Power Transformer
781 | HBI | HBI PLANT-B | 2 | 2 | 1 to 2 | EL2 | Power Transformer
782 | HBI | HBI PLANT-B | 3 | 3 | 3 to 5 | EE2 | Power Transformer
783 | HBI | HBI PLANT-B | 3 | 3 | 3 to 5 | EE-C | Power Transformer
784 | HBI | HBI PLANT-B | 2 | 2 | 1 to 2 | VPSA | Power Transformer
785 | HBI | HBI PLANT-B | 3 | 3 | 3 to 5 | T-261 | Power Transformer
786 | HBI | HBI PLANT-B | 3 | 3 | 3 to 5 | T-262 | Power Transformer
787 | HBI | HBI PLANT-B | 3 | 3 | 3 to 5 | T-263 | Power Transformer
788 | HBI | HBI PLANT-B | 1 | 1 | 1 to 2 | T-264 | Power Transformer
237 | HPL | 6.6 KV Line-Up - 1 | 31.5 | 31.5 | 21 to 50 | 072XG-009/01 | Power Transformer | Normal | Normal | 27.06.2025 | 69 | 24 | 0.02 | 0.0003 | 2721 | Not detected | 40.2 | 172 | 0.817 | 9 | 3 | 3 | 5 | BDL | 81 | 1646 | 5 | 42178 | 27726 | Normal | Normal | 2025 | Jun
238 | HPL | 6.6 KV Line-Up - 2 | 31.5 | 31.5 | 21 to 50 | 072XG-009/02 | Power Transformer | Normal | Normal | 27.06.2025 | 60 | 21 | 0.02 | 0.001 | 911 | Not detected | 37.6 | 164 | 0.822 | 8 | 3 | 3 | 5 | BDL | 81 | 1428 | 5 | 44336 | 29153 | Normal | Normal | 2025 | Jun
239 | HPL | EXCITATION TRANFO | 1.6 | 1.6 | 1 to 2 | 35698 | Power Transformer | Normal | Normal | 23.06.2025 | 79 | 23 | 0.02 | 0.03 | 885 | Not detected | 29.8 | 168 | 0.852 | 41 | 4 | 3 | 8 | BDL | 250 | 3851 | 11 | 41185 | 20822 | Normal | Normal | 2025 | Jun
240 | HPL | LSU 1.1 | 2 | 2 | 1 to 2 | 07-COC-074/01 | Power Transformer | Normal | Normal | 14.06.2025 | 45 | 34 | 0.02 | 0.001 | 237 | Not detected | 34.5 | 168 | 0.822 | 1 | 3 | 3 | 3 | BDL | 12 | 472 | 5 | 38767 | 28845 | Normal | Normal | 2025 | Jun
241 | HPL | LSU-1,ER-2 | 2 | 2 | 1 to 2 | 07COC074/02 | Power Transformer | Normal | Normal | 16.06.2025 | 67 | 19 | 0.02 | 0.0002 | 325 | Not detected | 37.5 | 162 | 0.817 | 1 | 3 | 3 | 4 | BDL | 129 | 1798 | 5 | 38532 | 26819 | Normal | Normal | 2025 | Jun
242 | HPL | LSU-1,ER-3 | 1.6 | 1.6 | 1 to 2 | 07CNC046/01 | Power Transformer | Normal | Normal | 24.06.2025 | 59 | 23 | 0.02 | 0.003 | 233 | Not detected | 35.3 | 162 | 0.817 | 5 | 3 | 3 | 10 | BDL | 135 | 1789 | 6 | 41527 | 28309 | Normal | Normal | 2025 | Jun
243 | HPL | LSU-1,ER-4 | 1.6 | 1.6 | 1 to 2 | 07CNC046/02 | Power Transformer | Normal | Normal | 21.06.2025 | 65 | 22 | 0.02 | 0.0005 | 800 | Not detected | 37.1 | 167 | 0.822 | 4 | 3 | 1 | 1 | BDL | 11 | 473 | 4 | 37314 | 25512 | Normal | Normal | 2025 | Jun
244 | HPL | LSU-1,ER-5 | 2 | 2 | 1 to 2 | 07COC074/03 | Power Transformer | Normal | Normal | 21.06.2025 | 53 | 27 | 0.02 | 0.0005 | 374 | Not detected | 37.2 | 166 | 0.827 | 1 | 3 | 3 | 4 | BDL | 30 | 909 | 5 | 39958 | 28528 | Normal | Normal | 2025 | Jun
245 | HPL | LSU-1,ER-6 | 1.25 | 1.25 | 1 to 2 | 07CMC022/04 | Power Transformer | Normal | Normal | 27.06.2025 | 66 | 19 | 0.02 | 0.0003 | 729 | Not detected | 44.6 | 172 | 0.822 | 4 | 3 | 3 | 4 | BDL | 88 | 1119 | 5 | 40582 | 28824 | Normal | Normal | 2025 | Jun
246 | HPL | LSU-2,ER-1 | 1.25 | 1.25 | 1 to 2 | 07CMC022/01 | Power Transformer | Normal | Normal | 16.06.2025 | 67 | 19 | 0.02 | 0.0002 | 325 | Not detected | 37.5 | 162 | 0.817 | 1 | 3 | 3 | 4 | BDL | 129 | 1798 | 5 | 38532 | 26819 | Normal | Normal | 2025 | Jun
247 | HPL | LSU-2,ER-2 | 2.5 | 2.5 | 3 to 5 | 07CPC030/01 | Power Transformer | Normal | Normal | 17.06.2025 | 57 | 29 | 0.02 | 0.0001 | 2204 | Not detected | 34.9 | 166 | 0.822 | 2 | 4 | 3 | 13 | BDL | 30 | 897 | 10 | 40405 | 27632 | Normal | Normal | 2025 | Jun
248 | HPL | LSU-2,ER-3 | 2 | 2 | 1 to 2 | 07COC075/01 | Power Transformer | Normal | Normal | 23.06.2025 | 67 | 26 | 0.02 | 0.002 | 256 | Not detected | 22.4 | 160 | 0.817 | 1 | 3 | 3 | 7 | BDL | 38 | 1046 | 6 | 41513 | 30217 | Normal | Normal | 2025 | Jun
249 | HPL | LSU-2,ER-4 | 2 | 2 | 1 to 2 | 07COC075/02 | Power Transformer | Normal | Normal | 21.06.2025 | 47 | 35 | 0.02 | 0.001 | 1200 | Not detected | 38.5 | 166 | 0.827 | 4 | 3 | 3 | 4 | BDL | 25 | 1010 | 5 | 38435 | 28449 | Normal | Normal | 2025 | Jun
250 | HPL | LSU-2,ER-5 | 2.5 | 2.5 | 3 to 5 | 07CPC031/01 | Power Transformer | Normal | Normal | 21.06.2025 | 52 | 20 | 0.02 | 0.0008 | 854 | Not detected | 36 | 166 | 0.827 | 1 | 3 | 3 | 4 | BDL | 31 | 576 | 5 | 40615 | 29270 | Normal | Normal | 2025 | Jun
251 | HPL | LSU-2,ER-6 | 2 | 2 | 1 to 2 | 07COC074/05 | Power Transformer | Normal | Normal | 28.06.2025 | 58 | 23 | 0.02 | 0.0003 | 929 | Not detected | 40 | 162 | 0.822 | 1 | 3 | 3 | 5 | BDL | 34 | 1075 | 6 | 43567 | 31376 | Normal | Normal | 2025 | Jun
252 | HPL | LSU-2.3 | 2.25 | 2.25 | 3 to 5 | 07-CPC-030/01 | Power Transformer | Normal | Normal | 20.06.2025 | 51 | 20 | 0.02 | 0.0003 | 1527 | Not detected | 37.4 | 164 | 0.822 | 2 | 6 | 4 | 22 | BDL | 36 | 569 | 10 | 39319 | 27818 | Normal | Normal | 2025 | Jun
253 | HPL | LSU-3,ER-2 | 2.5 | 2.5 | 3 to 5 | 07CPC030/02 | Power Transformer | Normal | Normal | 23.06.2025 | 67 | 26 | 0.02 | 0.002 | 256 | Not detected | 22.4 | 160 | 0.817 | 1 | 3 | 3 | 7 | BDL | 38 | 1046 | 6 | 41513 | 30217 | Normal | Normal | 2025 | Jun
254 | HPL | LSU-3,ER-3 | 1.25 | 1.25 | 1 to 2 | 07CMC022/02 | Power Transformer | Normal | Normal | 26.06.2025 | 68 | 18 | 0.02 | 0.003 | 1576 | Not detected | 39.7 | 168 | 0.854 | 5 | 3 | 3 | 5 | BDL | 125 | 1205 | 6 | 41240 | 28209 | Normal | Normal | 2025 | Jun
255 | HPL | LSU-3,ER-5 | 2 | 2 | 1 to 2 | 07COC074/04 | Power Transformer | Normal | Normal | 21.06.2025 | 64 | 23 | 0.02 | 0.0003 | 1371 | Not detected | 37.5 | 168 | 0.817 | 1 | 3 | 3 | 4 | BDL | 38 | 986 | 5 | 40828 | 29110 | Normal | Normal | 2025 | Jun
256 | HPL | LSU-4,ER-2 | 1.25 | 1.25 | 1 to 2 | 07CMC023/01 | Power Transformer | Normal | Normal | 20.06.2025 | 47 | 35 | 0.02 | 0.001 | 1200 | Not detected | 38.5 | 166 | 0.827 | 4 | 3 | 3 | 4 | BDL | 25 | 1010 | 5 | 38435 | 28449 | Normal | Normal | 2025 | Jun
257 | HPL | LSU-4,ER-3 | 1.25 | 1.25 | 1 to 2 | 07CMC022/03 | Power Transformer | Normal | Normal | 26.06.2025 | 79 | 16 | 0.02 | 0.003 | 654 | Not detected | 43.7 | 162 | 0.822 | 7 | 4 | 3 | 3 | BDL | 166 | 1746 | 6 | 41832 | 27558 | Normal | Normal | 2025 | Jun
258 | HPL | LSU-4,ER-5 | 3.5 | 3.5 | 3 to 5 | 07CQC020/01 | Power Transformer | Normal | Normal | 23.06.2025 | 58 | 24 | 0.02 | 0.001 | 688 | Not detected | 39.3 | 164 | 0.822 | 2 | 3 | 3 | 5 | BDL | 49 | 1340 | 5 | 38173 | 27450 | Normal | Normal | 2025 | Jun
259 | HPL | MAIN DRIVE TRAFO BOTTOM - 3.1 | 4.1 | 4.1 | 3 to 5 | 35693 | Power Transformer | Normal | Normal | 21.06.2025 | 71 | 20 | 0.02 | 0.01 | 18 | Not detected | 23.6 | 154 | 0.852 | 9 | 4 | 3 | 4 | BDL | 163 | 1564 | 6 | 37560 | 21520 | Normal | Normal | 2025 | Jun
260 | HPL | MAIN DRIVE TRAFO BOTTOM - 3.2 | 4.1 | 4.1 | 3 to 5 | 35695 | Power Transformer | Normal | Normal | 21.06.2025 | 77 | 14 | 0.02 | 0.01 | 15 | Not detected | 25.9 | 152 | 0.842 | 15 | 4 | 3 | 6 | BDL | 172 | 1861 | 7 | 38312 | 21616 | Normal | Normal | 2025 | Jun
261 | HPL | MAIN DRIVE TRAFO BOTTOM - 3.3 | 4.1 | 4.1 | 3 to 5 | 35697 | Power Transformer | Normal | Normal | 23.06.2025 | 73 | 21 | 0.02 | 0.01 | 18 | Not detected | 24.9 | 156 | 0.842 | 14 | 4 | 3 | 3 | BDL | 187 | 2139 | 7 | 38768 | 21982 | Normal | Normal | 2025 | Jun
262 | HPL | MAIN DRIVE TRAFO TOP - 2.1 | 4.1 | 4.1 | 3 to 5 | 35692 | Power Transformer | Normal | Normal | 18.06.2025 | 54 | 20 | 0.02 | 0.0112 | 18 | Not detected | 23.5 | 154 | 0.862 | 12 | 4 | 3 | 5 | BDL | 169 | 1571 | 5 | 36180 | 20308 | Normal | Normal | 2025 | Jun
263 | HPL | MAIN DRIVE TRAFO TOP - 2.2 | 4.1 | 4.1 | 3 to 5 | 35694 | Power Transformer | Normal | Normal | 19.06.2025 | 60 | 19 | 0.02 | 0.0113 | 17 | Not detected | 22.8 | 156 | 0.862 | 15 | 5 | 3 | 6 | BDL | 183 | 1994 | 6 | 36050 | 19595 | Normal | Normal | 2025 | Jun
264 | HPL | MAIN DRIVE TRAFO TOP - 2.3 | 4.1 | 4.1 | 3 to 5 | 35696 | Power Transformer | Normal | Normal | 19.06.2025 | 66 | 16 | 0.02 | 0.01 | 15 | Not detected | 24.3 | 158 | 0.862 | 14 | 5 | 3 | 3 | BDL | 171 | 1675 | 7 | 34340 | 19038 | Normal | Normal | 2025 | Jun
265 | HPL | PCC - 1.1 | 2 | 2 | 1 to 2 | 07OC076/R1 | Power Transformer | Normal | Normal | 16.06.2025 | 58 | 21 | 0.02 | 0.00019 | 856 | Not detected | 36.2 | 160 | 0.822 | 1 | 3 | 3 | 4 | BDL | 26 | 857 | 5 | 45035 | 32124 | Normal | Normal | 2025 | Jun
266 | HPL | PCC - 3.1 | 2 | 2 | 1 to 2 | 07OC076/R5 | Power Transformer | Normal | Normal | 28.06.2025 | 85 | 13 | 0.02 | 0.01 | 962 | Not detected | 43.5 | 168 | 0.817 | 1 | 3 | 3 | 5 | BDL | 29 | 1081 | 6 | 42287 | 31170 | Normal | Normal | 2025 | Jun
267 | HPL | PCC - 3.2 | 2 | 2 | 1 to 2 | 07OC076/R6 | Power Transformer | Normal | Normal | 29.06.2025 | 75 | 28 | 0.02 | 0.0003 | 2608 | Not detected | 43.3 | 166 | 0.817 | 1 | 3 | 3 | 6 | BDL | 38 | 1397 | 7 | 41888 | 30593 | Normal | Normal | 2025 | Jun
268 | HPL | PCC - 3.3 | 2 | 2 | 1 to 2 | 07OC076/R7 | Power Transformer | Normal | Normal | 29.06.2025 | 63 | 34 | 0.02 | 0.0003 | 608 | Not detected | 36 | 160 | 0.817 | 1 | 6 | 4 | 15 | BDL | 29 | 1027 | 18 | 45169 | 33096 | Normal | Normal | 2025 | Jun
269 | HPL | PCC - 3.4 | 2 | 2 | 1 to 2 | 07OC076/R8 | Power Transformer | Normal | Normal | 26.06.2025 | 59 | 23 | 0.02 | 0.0004 | 1260 | Not detected | 37.6 | 164 | 0.817 | 1 | 3 | 3 | 3 | BDL | 47 | 1302 | 6 | 43865 | 31873 | Normal | Normal | 2025 | Jun
270 | HPL | PCC - 4.1 | 2 | 2 | 1 to 2 | 07OC076/R9 | Power Transformer | Normal | Normal | 25.06.2025 | 63 | 31 | 0.02 | 0.0009 | 325 | Not detected | 36.8 | 160 | 0.817 | 1 | 3 | 3 | 4 | BDL | 28 | 868 | 5 | 43159 | 31670 | Normal | Normal | 2025 | Jun
271 | HPL | PCC - 5.1 | 2 | 2 | 1 to 2 | 07OC076/R10 | Power Transformer | Normal | Normal | 25.06.2025 | 63 | 23 | 0.02 | 0.03 | 418 | Not detected | 35.1 | 156 | 0.822 | 1 | 3 | 3 | 3 | BDL | 28 | 537 | 5 | 39897 | 28890 | Normal | Normal | 2025 | Jun
272 | HPL | PCC - 6.1 | 2 | 2 | 1 to 2 | 07OC076/R11 | Power Transformer | Normal | Normal | 26.06.2025 | 52 | 25 | 0.02 | 0.0001 | 731 | Not detected | 41.6 | 162 | 0.817 | 1 | 3 | 3 | 4 | BDL | 25 | 682 | 5 | 42143 | 31012 | Normal | Normal | 2025 | Jun
273 | HPL | PCC - 6.2 | 2 | 2 | 1 to 2 | 07OC076/R12 | Power Transformer | Normal | Normal | 26.06.2025 | 55 | 26 | 0.02 | 0.0003 | 2044 | Not detected | 40.9 | 168 | 0.817 | 1 | 3 | 3 | 4 | BDL | 25 | 913 | 5 | 40353 | 30042 | Normal | Normal | 2025 | Jun
274 | HPL | PCC - 6.3 | 2 | 2 | 1 to 2 | 07OC076/R13 | Power Transformer | Normal | Normal | 27.06.2025 | 55 | 26 | 0.02 | 0.0003 | 2044 | Not detected | 40.9 | 168 | 0.817 | 1 | 3 | 3 | 4 | BDL | 29 | 696 | 5 | 41574 | 30998 | Normal | Normal | 2025 | Jun
275 | HPL | PCC - 7.1 | 2 | 2 | 1 to 2 | 07OC076/R14 | Power Transformer | Normal | Normal | 28.06.2025 | 68 | 28 | 0.02 | 0.0001 | 2242 | Not detected | 38.8 | 162 | 0.817 | 1 | 3 | 3 | 3 | BDL | 24 | 694 | 5 | 40815 | 29353 | Normal | Normal | 2025 | Jun
276 | HPL | PCC - 7.2 | 2 | 2 | 1 to 2 | 07OC076/R15 | Power Transformer | Normal | Normal | 28.06.2025 | 73 | 19 | 0.02 | 0.001 | 865 | Not detected | 37.9 | 164 | 0.817 | 1 | 3 | 3 | 4 | BDL | 35 | 1666 | 6 | 42032 | 29353 | Normal | Normal | 2025 | Jun
277 | HPL | PCC - 7.3 | 2 | 2 | 1 to 2 | 07OC076/R16 | Power Transformer | Normal | Normal | 28.06.2025 | 72 | 23 | 0.02 | 0.0002 | 677 | Not detected | 42.3 | 162 | 0.817 | 1 | 4 | 6 | 31 | BDL | 28 | 1402 | 28 | 42474 | 31212 | Normal | Normal | 2025 | Jun
278 | HPL | PCC -1.2 | 2 | 2 | 1 to 2 | 07OC076/R2 | Power Transformer | Normal | Normal | 16.06.2025 | 68 | 21 | 0.02 | 0.0007 | 1731 | Not detected | 36.6 | 162 | 0.822 | 1 | 3 | 3 | 5 | BDL | 30 | 838 | 5 | 40381 | 29628 | Normal | Normal | 2025 | Jun
279 | HPL | PCC 2.1 | 2 | 2 | 1 to 2 | 07OC076/R3 | Power Transformer | Normal | Moderate | 17.06.2025 | 44 | 45 | 0.02 | 0.0002 | 877 | Not detected | 35.4 | 165 | 0.822 | 1 | 3 | 3 | 3 | BDL | 30 | 714 | 5 | 37303 | 25149 | Normal | Moderate | 2025 | Jun
280 | HPL | PCC 2.2 | 2 | 2 | 1 to 2 | 07OC076/R4 | Power Transformer | Normal | Normal | 28.12.2024 | 59 | 22 | NA | NA | NA | NA | NA | NA | NA | 4 | 17 | 10 | 62 | 2 | 28 | 1108 | 39 | 68078 | 40145 | Normal | Normal | 2024 | Dec
281 | HPL | PCC-6.4 | 2 | 2 | 1 to 2 | 07OC76/17 | Power Transformer | Normal | Normal | 27.06.2025 | 54 | 24 | 0.02 | 0.0003 | 1998 | Not detected | 43.5 | 162 | 0.817 | 1 | 3 | 3 | 4 | BDL | 29 | 811 | 5 | 40910 | 30680 | Normal | Normal | 2025 | Jun
282 | HSM | 30 MVA -1 | 30 | 30 | 21 to 50 | 2800054001 | Power Transformer | Normal | Normal | 29.05.2025 | 56 | 36 | 0.02 | 0.002 | 81 | Not detected | 32 | 162 | 0.832 | 3 | 4 | 3 | 5 | BDL | 74 | 590 | 6 | 43159 | 30898 | Normal | Normal | 2025 | May
283 | HSM | 30 MVA -2 | 30 | 30 | 21 to 50 | 2800054002 | Power Transformer | Normal | Normal | 29.05.2025 | 50 | 26 | 0.02 | 0.001 | 426 | Not detected | 33 | 168 | 0.837 | 2 | 4 | 3 | 4 | BDL | 76 | 630 | 5 | 43181 | 30010 | Normal | Normal | 2025 | May
284 | HSM | FM MD 1-A | 6 | 6 | 6 to 10 | SPL-2695 | Power Transformer | Normal | Normal | 14.05.2025 | 60 | 12 | 0.02 | 0.001 | 1183 | Not detected | 40 | 168 | 0.827 | 42 | 3 | 2 | 3 | BDL | 308 | 1053 | 3 | 21854 | 6612 | Normal | Normal | 2025 | May
285 | HSM | FM MD 1-B | 6 | 6 | 6 to 10 | SPL-2692 | Power Transformer | Normal | Normal | 14.05.2025 | 57 | 10 | 0.02 | 0.001 | 1448 | Not detected | 39.4 | 170 | 0.837 | 34 | 3 | 2 | 9 | BDL | 288 | 1119 | 4 | 25102 | 5816 | Normal | Normal | 2025 | May
286 | HSM | FM MD 2-A | 6 | 6 | 6 to 10 | SPL-2751 | Power Transformer | Normal | Normal | 12.05.2025 | 63 | 7 | 0.02 | 0.0004 | 1014 | Not detected | 36.5 | 178 | 0.832 | 49 | 2 | 2 | 3 | BDL | 223 | 800 | 2 | 22122 | 4071 | Normal | Normal | 2025 | May
287 | HSM | FM MD 2-B | 6 | 6 | 6 to 10 | SPL-2693 | Power Transformer | Normal | Normal | 14.05.2025 | 58 | 10 | 0.02 | 0.001 | 661 | Not detected | 38.6 | 174 | 0.827 | 24 | 2 | 3 | 4 | BDL | 184 | 1161 | 5 | 38247 | 9165 | Normal | Normal | 2025 | May
288 | HSM | FM MD 3-A | 6 | 6 | 6 to 10 | SPL-2651 | Power Transformer | Normal | Normal | 12.05.2025 | 58 | 10 | 0.02 | 0.001 | 661 | Not detected | 38.6 | 174 | 0.827 | 37 | 2 | 3 | 3 | BDL | 359 | 1350 | 4 | 28162 | 8468 | Normal | Normal | 2025 | May
289 | HSM | FM MD 3-B | 6 | 6 | 6 to 10 | SPL-2650 | Power Transformer | Normal | Normal | 12.05.2025 | 80 | 8 | 0.02 | 0.001 | 1161 | Not detected | 36.6 | 170 | 0.827 | 51 | 3 | 3 | 4 | BDL | 387 | 1469 | 5 | 39258 | 11469 | Normal | Normal | 2025 | May
290 | HSM | FM MD 4-A | 6 | 6 | 6 to 10 | SPL-2652 | Power Transformer | Normal | Normal | 12.05.2025 | 65 | 8 | 0.02 | 0.0004 | 2049 | Not detected | 39.6 | 172 | 0.822 | 44 | 2 | 3 | 5 | BDL | 430 | 1229 | 5 | 42015 | 11325 | Normal | Normal | 2025 | May
291 | HSM | FM MD 4-B | 6 | 6 | 6 to 10 | SPL-2649 | Power Transformer | Normal | Normal | 12.05.2025 | 47 | 39 | 0.02 | 0.001 | 1243 | Not detected | 37.6 | 172 | 0.822 | 33 | 2 | 2 | 3 | BDL | 305 | 1079 | 3 | 28952 | 7258 | Normal | Normal | 2025 | May
292 | HSM | FM MD 5-A | 3.4 | 3.4 | 3 to 5 | 92RG-020/1 | Power Transformer | Normal | Normal | 12.05.2025 | 52 | 27 | 0.02 | 0.0002 | 906 | Not detected | 38.7 | 168 | 0.827 | 6 | 3 | 3 | 4 | BDL | 78 | 1220 | 5 | 41254 | 17523 | Normal | Normal | 2025 | May
293 | HSM | FM MD 5-B | 3.4 | 3.4 | 3 to 5 | 92RG-021/2 | Power Transformer | Normal | Normal | 14.05.2025 | 57 | 20 | 0.02 | 0.001 | 165 | Not detected | 35.9 | 172 | 0.827 | 8 | 4 | 3 | 7 | BDL | 82 | 562 | 5 | 39816 | 14162 | Normal | Normal | 2025 | May
294 | HSM | FM MD 6-A | 3.4 | 3.4 | 3 to 5 | 92RG-020/2 | Power Transformer | Normal | Normal | 12.05.2025 | 58 | 28 | 0.02 | 0.001 | 485 | Not detected | 35.5 | 174 | 0.827 | 2 | 2 | 3 | 3 | BDL | 68 | 1348 | 5 | 42165 | 16187 | Normal | Normal | 2025 | May
295 | HSM | FM MD 6-B | 3.4 | 3.4 | 3 to 5 | 92RG-021/1 | Power Transformer | Normal | Normal | 14.05.2025 | 53 | 22 | 0.02 | 0.001 | 224 | Not detected | 30.4 | 176 | 0.827 | 3 | 3 | 3 | 4 | BDL | 63 | 898 | 5 | 40247 | 15383 | Normal | Normal | 2025 | May
296 | HSM | RM TOP - A | 6 | 6 | 6 to 10 | SPL-2748 | Power Transformer | Normal | Normal | 22.05.2025 | 59 | 8 | 0.02 | 0.0004 | 2085 | Not detected | 35.8 | 168 | 0.827 | 41 | 2 | 2 | 2 | BDL | 264 | 986 | 3 | 39912 | 13568 | Normal | Normal | 2025 | May
297 | HSM | RM TOP - B | 6 | 6 | 6 to 10 | SPL-2694 | Power Transformer | Normal | Normal | 22.05.2025 | 65 | 8 | 0.02 | 0.002 | 1320 | Not detected | 39.9 | 170 | 0.832 | 23 | 2 | 2 | 2 | BDL | 201 | 769 | 3 | 39812 | 14561 | Normal | Normal | 2025 | May
298 | HSM | RM BOT - A | 6 | 6 | 6 to 10 | SPL-2696 | Power Transformer | Normal | Normal | 22.05.2025 | 71 | 14 | 0.02 | 0.004 | 1328 | Not detected | 38.5 | 170 | 0.832 | 72 | 2 | 2 | 4 | BDL | 346 | 1469 | 3 | 41744 | 15707 | Normal | Normal | 2025 | May
299 | HSM | RM BOT - B | 6 | 6 | 6 to 10 | SPL-2752 | Power Transformer | Normal | Normal | 22.05.2025 | 66 | 8 | 0.02 | 0.003 | 2190 | Not detected | 37.6 | 168 | 0.832 | 39 | 2 | 2 | 3 | BDL | 320 | 1001 | 3 | 40268 | 14133 | Normal | Normal | 2025 | May
300 | HSM | VE-OPERATOR SIDE | 1.41 | 1.41 | 1 to 2 | 92MC-020/1 | Power Transformer | Normal | Normal | 16.05.2025 | 55 | 22 | 0.02 | 0.001 | 1343 | Not detected | 38.8 | 168 | 0.827 | 7 | 3 | 3 | 4 | BDL | 79 | 1303 | 5 | 38524 | 11404 | Normal | Normal | 2025 | May
301 | HSM | VE-DRIVE SIDE | 1.41 | 1.41 | 1 to 2 | 06MC-017/01 | Power Transformer | Normal | Normal | 16.05.2025 | 42 | 33 | 0.02 | 0.004 | 142 | Not detected | 31.2 | 170 | 0.827 | 5 | 2 | 3 | 5 | BDL | 110 | 1412 | 5 | 42963 | 12049 | Normal | Normal | 2025 | May
302 | HSM | COILER # 1 MANDREL | 1.3 | 1.3 | 1 to 2 | 92MC-003/1 | Power Transformer | Normal | Normal | 10.05.2025 | 55 | 27 | 0.02 | 0.003 | 96 | Not detected | 39.4 | 172 | 0.827 | 6 | 2 | 4 | 4 | BDL | 117 | 1651 | 6 | 42168 | 17122 | Normal | Normal | 2025 | May
303 | HSM | COILER # 2 MANDREL | 1.3 | 1.3 | 1 to 2 | 92MC-003/2 | Power Transformer | Normal | Normal | 10.05.2025 | 46 | 34 | 0.02 | 0.07 | 3 | Not detected | 24.3 | 168 | 0.832 | 57 | 2 | 2 | 5 | BDL | 378 | 2197 | 5 | 38201 | 8789 | Normal | Normal | 2025 | May
304 | HSM | CROP SHEAR | 2 | 2 | 1 to 2 | 06 COC 062/1 | Power Transformer | Normal | Normal | 14.05.2025 | 59 | 21 | 0.02 | 0.0003 | 1558 | Not detected | 40.2 | 170 | 0.832 | 1 | 2 | 3 | 3 | BDL | 30 | 1024 | 6 | 42963 | 17304 | Normal | Normal | 2025 | May
305 | HSM | LOAD CENTER # 1 | 2 | 2 | 1 to 2 | 910C-020/13 | Power Transformer | Normal | Moderate | 22.05.2025 | 49 | 42 | 0.02 | 0.03 | 8 | Not detected | 23 | 170 | 0.862 | 9 | 8 | 14 | 3 | BDL | 241 | 1521 | 11 | 42157 | 13501 | Normal | Moderate | 2025 | May
306 | HSM | LOAD CENTER # 2 | 2 | 2 | 1 to 2 | 910C-020/9 | Power Transformer | Normal | Moderate | 22.05.2025 | 47 | 46 | 0.02 | 0.09 | 5 | Not detected | 20.5 | 172 | 0.862 | 6 | 1 | 11 | 3 | BDL | 235 | 1221 | 10 | 40622 | 6119 | Normal | Moderate | 2025 | May
307 | HSM | LOAD CENTER # 3 | 2 | 2 | 1 to 2 | 910C-020/12 | Power Transformer | Normal | Moderate | 16.05.2025 | 45 | 60 | 0.02 | 0.06 | 3 | Not detected | 20.7 | 174 | 0.852 | 6 | 28 | 8 | 3 | BDL | 275 | 1002 | 6 | 35476 | 4109 | Normal | Moderate | 2025 | May
308 | HSM | LOAD CENTER # 4 | 2 | 2 | 1 to 2 | 910C-020/15 | Power Transformer | Normal | Normal | 16.05.2025 | 53 | 30 | 0.02 | 0.007 | 69 | Not detected | 31.5 | 172 | 0.852 | 5 | 2 | 2 | 2 | BDL | 86 | 1110 | 3 | 36854 | 8695 | Normal | Normal | 2025 | May
309 | HSM | LOAD CENTER # 5 | 2 | 2 | 1 to 2 | 910C-020/1 | Power Transformer | Normal | Normal | 16.05.2025 | 65 | 27 | 0.02 | 0.04 | 7 | Not detected | 21.4 | 160 | 0.852 | 14 | 20 | 6 | 6 | BDL | 328 | 565 | 6 | 31432 | 3431 | Normal | Normal | 2025 | May
310 | HSM | LOAD CENTER # 6 | 2 | 2 | 1 to 2 | 910C-020/10 | Power Transformer | Normal | Normal | 16.05.2025 | 45 | 39 | 0.02 | 0.06 | 4 | Not detected | 21.5 | 164 | 0.852 | 13 | 6 | 4 | 4 | BDL | 429 | 1277 | 8 | 32459 | 4998 | Normal | Normal | 2025 | May
311 | HSM | LOAD CENTER # 7 | 2 | 2 | 1 to 2 | 910C-020/4 | Power Transformer | Normal | Normal | 12.05.2025 | 52 | 32 | 0.02 | 0.03 | 7 | Not detected | 21.4 | 164 | 0.852 | 22 | 4 | 3 | 11 | BDL | 562 | 1308 | 7 | 32547 | 3651 | Normal | Normal | 2025 | May
312 | HSM | LOAD CENTER # 8 | 2 | 2 | 1 to 2 | 910C-020/5 | Power Transformer | Normal | Normal | 12.05.2025 | 47 | 38 | 0.02 | 0.03 | 5 | Not detected | 22 | 172 | 0.857 | 14 | 10 | 3 | 3 | BDL | 483 | 1563 | 7 | 38597 | 4697 | Normal | Normal | 2025 | May
313 | HSM | LOAD CENTER # 9 | 2 | 2 | 1 to 2 | 910C-020/2 | Power Transformer | Normal | Normal | 12.05.2025 | 49 | 37 | 0.02 | 0.04 | 7 | Not detected | 23.5 | 172 | 0.857 | 55 | 4 | 3 | 3 | BDL | 409 | 851 | 6 | 39752 | 5671 | Normal | Normal | 2025 | May
314 | HSM | LOAD CENTER # 10 | 2 | 2 | 1 to 2 | 910C-020/8 | Power Transformer | Normal | Normal | 10.05.2025 | 54 | 20 | 0.02 | 0.04 | 5 | Not detected | 25.9 | 160 | 0.847 | 17 | 11 | 4 | 3 | BDL | 256 | 480 | 5 | 28547 | 3549 | Normal | Normal | 2025 | May
315 | HSM | LOAD CENTER # 11 | 2 | 2 | 1 to 2 | 910C-020/7 | Power Transformer | Normal | Moderate | 10.05.2025 | 43 | 48 | 0.02 | 0.06 | 3 | Not detected | 23.4 | 158 | 0.857 | 8 | 15 | 3 | 2 | BDL | 215 | 1025 | 4 | 26512 | 3537 | Normal | Moderate | 2025 | May
316 | HSM | LOAD CENTER # 12 | 2 | 2 | 1 to 2 | 910C-020/6 | Power Transformer | Normal | Normal | 10.05.2025 | 42 | 38 | 0.02 | 0.07 | 3 | Not detected | 22.4 | 172 | 0.862 | 7 | 8 | 5 | 5 | BDL | 277 | 571 | 7 | 31254 | 5649 | Normal | Normal | 2025 | May
317 | HSM | LOAD CENTER # 13 | 2 | 2 | 1 to 2 | 910C-020/3 | Power Transformer | Normal | Normal | 10.05.2025 | 43 | 39 | 0.02 | 0.09 | 2 | Not detected | 22.2 | 168 | 0.862 | 34 | 16 | 8 | 3 | BDL | 318 | 1161 | 8 | 27541 | 3067 | Normal | Normal | 2025 | May
318 | HSM | LOAD CENTER # 14 | 2 | 2 | 1 to 2 | 930C-023/4 | Power Transformer | Normal | Normal | 29.05.2025 | 55 | 26 | 0.02 | 0.009 | 28 | Not detected | 29.2 | 164 | 0.852 | 20 | 10 | 5 | 5 | BDL | 205 | 3337 | 8 | 43897 | 20596 | Normal | Normal | 2025 | May
319 | HSM | LOAD CENTER # 15 | 2 | 2 | 1 to 2 | 930C-023/1 | Power Transformer | Normal | Moderate | 29.05.2025 | 44 | 43 | 0.02 | 0.06 | 3 | Not detected | 22 | 158 | 0.857 | 21 | 8 | 3 | 6 | BDL | 426 | 1698 | 8 | 43076 | 9068 | Normal | Moderate | 2025 | May
320 | HSM | LOAD CENTER # 16 | 2 | 2 | 1 to 2 | 930C-020/11 | Power Transformer | Normal | Normal | 29.05.2025 | 55 | 38 | 0.02 | 0.02 | 14 | Not detected | 25.7 | 158 | 0.852 | 8 | 4 | 3 | 3 | BDL | 228 | 1859 | 5 | 39095 | 11433 | Normal | Normal | 2025 | May
321 | HSM | LOAD CENTER # 17 | 2 | 2 | 1 to 2 | 910C-020/14 | Power Transformer | Normal | Normal | 29.05.2025 | 46 | 39 | 0.02 | 0.03 | 7 | Not detected | 29.2 | 160 | 0.852 | 19 | 9 | 4 | 6 | BDL | 401 | 2191 | 9 | 54373 | 10977 | Normal | Normal | 2025 | May
322 | HSM | SPARE - FM/RM MD | 3.9 | 3.9 | 3 to 5 | 92RG-019/2 | Power Transformer | Normal | Normal | 30.05.2025 | 54 | 24 | 0.02 | 0.003 | 165 | Not detected | 36.4 | 164 | 0.832 | 27 | 4 | 3 | 4 | BDL | 116 | 789 | 5 | 39960 | 26610 | Normal | Normal | 2025 | May
323 | HSM | SPARE - CS | 2 | 2 | 1 to 2 | 92OC-022/1 | Power Transformer | Normal | Normal | 30.05.2025 | 51 | 16 | 0.02 | 0.001 | 536 | Not detected | 33.8 | 160 | 0.832 | 4 | 4 | 3 | 4 | BDL | 71 | 812 | 5 | 39124 | 28619 | Normal | Normal | 2025 | May
324 | HSM | SPARE - LOAD CENTER | 2 | 2 | 1 to 2 | 910C-020/1 | Power Transformer | Normal | Normal | 30.05.2025 | 54 | 17 | 0.03 | 0.02 | 24 | Not detected | 28.8 | 162 | 0.832 | 2 | 4 | 3 | 7 | BDL | 82 | 691 | 5 | 36177 | 25529 | Normal | Normal | 2025 | May
325 | HSM | SPARE - CLR/ VE | 1.41 | 1.41 | 1 to 2 | 92NC-21/1 | Power Transformer | Normal | Normal | 30.05.2025 | 55 | 22 | 0.02 | 0.04 | 236 | Not detected | 35.4 | 168 | 0.832 | 14 | 4 | 3 | 4 | BDL | 54 | 1212 | 5 | 48514 | 28951 | Normal | Normal | 2025 | May
326 | HSM | SPARE - CLR/ VE | 1.41 | 1.41 | 1 to 2 | 52427 | Power Transformer | Normal | Normal | 30.05.2025 | 67 | 10 | 0.02 | 0.0002 | 2679 | Not detected | 42.1 | 172 | 0.832 | 21 | 3 | 2 | 3 | BDL | 63 | 1422 | 4 | 43749 | 23410 | Normal | Normal | 2025 | May
900 | HSM | BC BAY | 30 | 30 | 21 to 50 | 30 MVA -1 | Power Transformer
901 | HSM | BC BAY | 30 | 30 | 21 to 50 | 30 MVA -2 | Power Transformer
902 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 1-A | Power Transformer
903 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 1-B | Power Transformer
904 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 2-A | Power Transformer
905 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 2-B | Power Transformer
906 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 3-A | Power Transformer
907 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 3-B | Power Transformer
908 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 4-A | Power Transformer
909 | HSM | BC BAY | 6 | 6 | 6 to 10 | FM MD 4-B | Power Transformer
910 | HSM | BC BAY | 3.4 | 3.4 | 3 to 5 | FM MD 5-A | Power Transformer
911 | HSM | BC BAY | 3.4 | 3.4 | 3 to 5 | FM MD 5-B | Power Transformer
912 | HSM | BC BAY | 3.4 | 3.4 | 3 to 5 | FM MD 6-A | Power Transformer
913 | HSM | BC BAY | 3.4 | 3.4 | 3 to 5 | FM MD 6-B | Power Transformer
914 | HSM | BC BAY | 6 | 6 | 6 to 10 | RM TOP - A | Power Transformer
915 | HSM | BC BAY | 6 | 6 | 6 to 10 | RM TOP - B | Power Transformer
916 | HSM | BC BAY | 6 | 6 | 6 to 10 | RM BOT - A | Power Transformer
917 | HSM | BC BAY | 6 | 6 | 6 to 10 | RM BOT - B | Power Transformer
918 | HSM | BC BAY | 1.41 | 1.41 | 1 to 2 | VE-OPERATOR SIDE | Power Transformer
919 | HSM | BC BAY | 1.41 | 1.41 | 1 to 2 | VE-DRIVE SIDE | Power Transformer
920 | HSM | BC BAY | 1.3 | 1.3 | 1 to 2 | COILER # 1 MANDREL | Power Transformer
921 | HSM | BC BAY | 1.3 | 1.3 | 1 to 2 | COILER # 2 MANDREL | Power Transformer
922 | HSM | BC BAY | 2 | 2 | 1 to 2 | CROP SHEAR | Power Transformer
923 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 1 | Power Transformer
924 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 2 | Power Transformer
925 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 3 | Power Transformer
926 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 4 | Power Transformer
927 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 5 | Power Transformer
928 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 6 | Power Transformer
929 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 7 | Power Transformer
930 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 8 | Power Transformer
931 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 9 | Power Transformer
932 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 10 | Power Transformer
933 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 11 | Power Transformer
934 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 12 | Power Transformer
935 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 13 | Power Transformer
936 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 14 | Power Transformer
937 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 15 | Power Transformer
938 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 16 | Power Transformer
939 | HSM | BC BAY | 2 | 2 | 1 to 2 | LOAD CENTER # 17 | Power Transformer
940 | HSM | BC BAY | 3.9 | 3.9 | 3 to 5 | SPARE - FM/RM MD | Power Transformer
942 | HSM | BC BAY | 2 | 2 | 1 to 2 | SPARE - CS | Power Transformer
943 | HSM | BC BAY | 2 | 2 | 1 to 2 | SPARE - LOAD CENTER | Power Transformer
944 | HSM | BC BAY | 1.41 | 1.41 | 1 to 2 | SPARE - CLR/ VE | Power Transformer
1091 | LOGISTICS | TPA ECR | 1.5 | 1.5 | 1 to 2 | TANKER PARKING - 1.5MVA | Power Transformer
327 | MH | ECR-1 POWER T/F-1 | 20/25 | 20 | 11 to 20 | 07 ZG010/03 | Power Transformer | Normal | Normal | 07.04.2025 | 71 | 15 | 0.02 | 0.001 | 657 | Not detected | 39.9 | 160 | 0.827 | 2 | 2 | 3 | 6 | BDL | 55 | 1223 | 5 | 45215 | 28397 | Normal | Normal | 2025 | Apr
328 | MH | ECR-1 POWER T/F-2 | 20/25 | 20 | 11 to 20 | 07 ZG010/04 | Power Transformer | Normal | Normal | 07.04.2025 | 54 | 25 | 0.02 | 0.001 | 1233 | Not detected | 36.2 | 158 | 0.827 | 2 | 2 | 3 | 10 | BDL | 59 | 1558 | 8 | 47233 | 28941 | Normal | Normal | 2025 | Apr
329 | MH | ECR-1 DIST. T/F-1 | 2 | 2 | 1 to 2 | 07 OC-064/1 | Power Transformer | Normal | Normal | 07.04.2025 | 55 | 14 | 0.02 | 0.001 | 650 | Not detected | 41.9 | 158 | 0.827 | 2 | 2 | 3 | 3 | BDL | 49 | 1459 | 5 | 47012 | 25083 | Normal | Normal | 2025 | Apr
330 | MH | ECR-1 DIST. T/F-2 | 2.35 | 2.35 | 3 to 5 | 951593-2 | Power Transformer | Normal | Normal | 07.04.2025 | 55 | 18 | 0.02 | 0.001 | 1246 | Not detected | 37.4 | 162 | 0.827 | 2 | 2 | 3 | 4 | BDL | 48 | 1368 | 5 | 47171 | 27801 | Normal | Normal | 2025 | Apr
331 | MH | ECR-1 DIST. T/F-3 | 2 | 2 | 1 to 2 | 07 OC-064/19 | Power Transformer | Normal | Normal | 07.04.2025 | 58 | 20 | 0.02 | 0.0005 | 1168 | Not detected | 39.3 | 162 | 0.827 | 3 | 2 | 5 | 26 | BDL | 55 | 1292 | 13 | 49745 | 31622 | Normal | Normal | 2025 | Apr
332 | MH | LCP-MH T/F | 2.5 | 2.5 | 3 to 5 | 08PC-041/01 | Power Transformer | Normal | Normal | 07.04.2025 | 68 | 14 | 0.02 | 0.002 | 1400 | Not detected | 38.5 | 172 | 0.827 | 1 | 2 | 2 | 3 | BDL | 34 | 994 | 5 | 46321 | 27339 | Normal | Normal | 2025 | Apr
333 | MH | SMP-MH T/F | 2 | 2 | 1 to 2 | 08OC-092/01 | Power Transformer | Normal | Moderate | 07.04.2025 | 36 | 52 | 0.02 | 0.001 | 832 | Not detected | 39.4 | 170 | 0.827 | 1 | 2 | 2 | 4 | BDL | 32 | 745 | 5 | 47917 | 29024 | Normal | Moderate | 2025 | Apr
334 | MH | MOD-6 T/F | 2 | 2 | 1 to 2 | 08OC-090/01 | Power Transformer | Normal | Normal | 07.04.2025 | 69 | 32 | 0.02 | 0.001 | 1770 | Not detected | 38.2 | 170 | 0.827 | 2 | 2 | 2 | 4 | BDL | 36 | 878 | 5 | 46758 | 29655 | Normal | Normal | 2025 | Apr
335 | MH | ECR-3 T/F-1 | 2 | 2 | 1 to 2 | 09-OC-101/01 | Power Transformer | Normal | Normal | 15.09.2025 | 55 | 10 | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 3 | 5 | BDL | 40 | 1135 | 4 | 40196 | 21916 | Normal | Normal | 2025 | Sep
336 | MH | ECR-3 T/F-2 | 2.35 | 2.35 | 3 to 5 | 951593-1 | Power Transformer | Normal | Normal | 15.09.2025 | 55 | 39 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 3 | BDL | 117 | 2865 | 5 | 41112 | 21922 | Normal | Normal | 2025 | Sep
337 | MH | PHASE-2 T/F | 2 | 2 | 1 to 2 | 040C043/01 | Power Transformer | Normal | Normal | 31.03.2025 | 52 | 16 | 0.02 | 0.02 | 85 | Not detected | 34.7 | 174 | 0.827 | 1 | 2 | 3 | 3 | BDL | 23 | 800 | 5 | 42156 | 26831 | Normal | Normal | 2025 | Mar
338 | MH | MOD 5&6 T/F-1 | 2 | 2 | 1 to 2 | 05 OC 48/05 | Power Transformer | Normal | Normal | 15.09.2025 | 72 | 10 | NA | NA | NA | NA | NA | NA | NA | 10 | 2 | 3 | 7 | BDL | 176 | 1746 | 5 | 41922 | 20918 | Normal | Normal | 2025 | Sep
339 | MH | MOD 5&6 T/F-2 | 2 | 2 | 1 to 2 | 13746/1 | Power Transformer | Normal | Normal | 19.09.2025 | 51 | 23 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 5 | 6 | BDL | 96 | 2851 | 5 | 42154 | 22541 | Normal | Normal | 2025 | Sep
340 | MH | MH ECR POWER T/F-1 | 10/12 | 10 | 6 to 10 | 8637/1 | Power Transformer | Normal | Normal | 29.03.2025 | 62 | 16 | 0.02 | 0.002 | 178 | Not detected | 36.4 | 156 | 0.827 | 1 | 1 | 3 | 7 | BDL | 125 | 3677 | 6 | 42856 | 25236 | Normal | Normal | 2025 | Mar
341 | MH | MH ECR POWER T/F-2 | 10/12 | 10 | 6 to 10 | 8637/2 | Power Transformer | Normal | Normal | 29.03.2025 | 62 | 10 | 0.02 | 0.03 | 1010 | Not detected | 40.3 | 160 | 0.827 | 2 | 2 | 3 | 12 | BDL | 52 | 1939 | 5 | 42154 | 25472 | Normal | Normal | 2025 | Mar
342 | MH | MH ECR DIST. T/F-3 | 2 | 2 | 1 to 2 | 04OC047/01 | Power Transformer | Normal | Normal | 29.03.2025 | 56 | 15 | 0.02 | 0.0002 | 904 | Not detected | 35.4 | 172 | 0.827 | 3 | 2 | 3 | 3 | BDL | 92 | 1061 | 5 | 45265 | 25206 | Normal | Normal | 2025 | Mar
343 | MH | MH ECR DIST. T/F-4 | 2 | 2 | 1 to 2 | 8638/4 | Power Transformer | Normal | Normal | 29.03.2025 | 58 | 34 | 0.02 | 0.01 | 225 | Not detected | 37.3 | 172 | 0.827 | 1 | 2 | 3 | 5 | BDL | 40 | 3369 | 5 | 43156 | 20800 | Normal | Normal | 2025 | Mar
344 | MH | MH ECR DIST. T/F-5 | 2 | 2 | 1 to 2 | 8638/2 | Power Transformer | Normal | Normal | 29.03.2025 | 58 | 25 | 0.02 | 0.02 | 1041 | Not detected | 35.1 | 176 | 0.827 | 3 | 2 | 3 | 6 | BDL | 41 | 2045 | 5 | 42154 | 17826 | Normal | Normal | 2025 | Mar
345 | MH | MH ECR DIST. T/F-6 | 2 | 2 | 1 to 2 | 8638/3 | Power Transformer | Normal | Normal | 31.03.2025 | 51 | 18 | 0.02 | 0.004 | 453 | Not detected | 34.7 | 158 | 0.827 | 2 | 2 | 3 | 10 | BDL | 142 | 3773 | 5 | 41254 | 20497 | Normal | Normal | 2025 | Mar
346 | MH | MH ECR DIST. T/F-7 | 2 | 2 | 1 to 2 | 8638/1 | Power Transformer | Normal | Normal | 31.03.2025 | 52 | 18 | 0.02 | 0.004 | 456 | Not detected | 34.3 | 172 | 0.827 | 1 | 2 | 3 | 5 | BDL | 47 | 2913 | 5 | 42584 | 16278 | Normal | Normal | 2025 | Mar
347 | MH | MH ECR DIST. T/F-8 | 1 | 1 | 1 to 2 | 8639/2 | Power Transformer | Normal | Normal | 31.03.2025 | 31 | 33 | 0.02 | 0.002 | 496 | Not detected | 30.5 | 162 | 0.827 | 1 | 2 | 2 | 2 | BDL | 27 | 2912 | 4 | 42684 | 15765 | Normal | Normal | 2025 | Mar
348 | MH | MH ECR DIST. T/F-9 | 1 | 1 | 1 to 2 | 8639/1 | Power Transformer | Normal | Normal | 31.03.2023 | 69 | 29 | 0.02 | 0.001 | 2456 | Not detected | 31 | 154 | 0.832 | 1 | 3 | 4 | 5 | BDL | 27 | 1255 | 5 | 43156 | 14912 | Normal | Normal | 2023 | Mar
349 | MH | LCP2-MH DDS T/F | 2 | 2 | 1 to 2 | G.2429/1/21 | Power Transformer | Normal | Normal | 07.04.2025 | 62 | 23 | 0.02 | 0.003 | 269 | Not detected | 32.8 | 172 | 0.827 | 15 | 2 | 3 | 5 | BDL | 207 | 3301 | 5 | 46352 | 25023 | Normal | Normal | 2025 | Apr
350 | MH | ECR-4 POWER T/F-1 | 12.5/16.5 | 12.5 | 11 to 20 | TP95-8027 | Power Transformer | Normal | Normal | 14.09.2025 | 67 | 11 | NA | NA | NA | NA | NA | NA | NA | 13 | 2 | 2 | 2 | BDL | 22 | 914 | 4 | 42512 | 22580 | Normal | Normal | 2025 | Sep
351 | MH | ECR-4 POWER T/F-2 | 12/16.5 | 12 | 11 to 20 | TP95-8026-2 | Power Transformer | Normal | Normal | 14.09.2025 | 65 | 15 | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 3 | 3 | BDL | 20 | 597 | 5 | 44720 | 32828 | Normal | Normal | 2025 | Sep
352 | MH | ECR-4 DIST. T/F-1 | 2 | 2 | 1 to 2 | 07 OC-064/18 | Power Transformer | Normal | Normal | 14.09.2025 | 58 | 27 | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 2 | 3 | BDL | 25 | 700 | 4 | 42955 | 21832 | Normal | Normal | 2025 | Sep
353 | MH | ECR-4 DIST. T/F-2 | 2 | 2 | 1 to 2 | 08 OC-092/02 | Power Transformer | Normal | Normal | 14.09.2025 | 63 | 17 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 4 | BDL | 43 | 1363 | 5 | 42154 | 25625 | Normal | Normal | 2025 | Sep
354 | MH | ECR-4 DIST. T/F-3 | 2 | 2 | 1 to 2 | 09 OC-045/03 | Power Transformer | Normal | Normal | 14.09.2025 | 44 | 32 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 1 | 1 | BDL | 28 | 1517 | 5 | 42541 | 22484 | Normal | Normal | 2025 | Sep
355 | MH | LBSS TR | 2 | 2 | 1 to 2 | 07-OC-064/15 | Power Transformer | Normal | Normal | 15.09.2025 | 60 | 21 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 40 | 1529 | 5 | 41922 | 21902 | Normal | Normal | 2025 | Sep
1067 | MH | ECR-1 | 20/25 | 20 | 11 to 20 | ECR-1 POWER T/F-1 | Power Transformer
1068 | MH | ECR-1 | 20/25 | 20 | 11 to 20 | ECR-1 POWER T/F-2 | Power Transformer
1069 | MH | ECR-1 | 2 | 2 | 1 to 2 | ECR-1 DIST. T/F-1 | Power Transformer
1070 | MH | ECR-1 | 2.35 | 2.35 | 3 to 5 | ECR-1 DIST. T/F-2 | Power Transformer
1071 | MH | ECR-1 | 2 | 2 | 1 to 2 | ECR-1 DIST. T/F-3 | Power Transformer
1072 | MH | ECR-2 | 2.5 | 2.5 | 3 to 5 | LCP-MH T/F | Power Transformer
1073 | MH | SMP-MH ECR | 2 | 2 | 1 to 2 | SMP-MH T/F | Power Transformer
1074 | MH | SMP-MH ECR | 2 | 2 | 1 to 2 | MOD-6 T/F | Power Transformer
1075 | MH | ECR-3 | 2 | 2 | 1 to 2 | ECR-3 T/F-1 | Power Transformer
1076 | MH | ECR-3 | 2.35 | 2.35 | 3 to 5 | ECR-3 T/F-2 | Power Transformer
1077 | MH | SS-15 | 2 | 2 | 1 to 2 | PHASE-2 T/F | Power Transformer
1078 | MH | MH-M5&6-ECR | 2 | 2 | 1 to 2 | MOD 5&6 T/F-1 | Power Transformer
1079 | MH | MH-M5&6-ECR | 2 | 2 | 1 to 2 | MOD 5&6 T/F-2 | Power Transformer
1080 | MH | MH ECR | 10/12 | 10 | 6 to 10 | MH ECR POWER T/F-1 | Power Transformer
1081 | MH | MH ECR | 10/12 | 10 | 6 to 10 | MH ECR POWER T/F-2 | Power Transformer
1082 | MH | MH ECR | 2 | 2 | 1 to 2 | MH ECR DIST. T/F-3 | Power Transformer
1083 | MH | MH ECR | 2 | 2 | 1 to 2 | MH ECR DIST. T/F-4 | Power Transformer
1084 | MH | MH ECR | 2 | 2 | 1 to 2 | MH ECR DIST. T/F-5 | Power Transformer
1085 | MH | MH ECR | 2 | 2 | 1 to 2 | MH ECR DIST. T/F-6 | Power Transformer
1086 | MH | MH ECR | 2 | 2 | 1 to 2 | MH ECR DIST. T/F-7 | Power Transformer
1087 | MH | MH ECR | 1 | 1 | 1 to 2 | MH ECR DIST. T/F-8 | Power Transformer
1088 | MH | MH ECR | 1 | 1 | 1 to 2 | MH ECR DIST. T/F-9 | Power Transformer
356 | MRSS | 100MVA TR -1 | 135 | 135 | 101 to 200 | 6800000118 | Power Transformer | Normal |  | 05.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 5 | 5 | 3 | 7 | 3 | 198 | 1965 | 5 | 44633 | 309512 | Normal |  | 2025 | Jul
357 | MRSS | 100MVA TR -2 | 100/140 | 100 | 51 to 100 | 6800000119 | Power Transformer | Normal |  | 05.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 24 | 10 | 2 | 8 | BDL | 822 | 4702 | 4 | 45811 | 14623 | Normal |  | 2025 | Jul
358 | MRSS | 100MVA TR -3 | 100 | 100 | 51 to 100 | 2015632 | Power Transformer | Normal |  | 14.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 10 | 3 | 3 | 3 | BDL | 152 | 1824 | 5 | 48052 | 29525 | Normal |  | 2025 | Jul
359 | MRSS | 135MVA TR -1 | 135 | 135 | 101 to 200 | 6800000120 | Power Transformer | Normal |  | 05.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 27 | 5 | 2 | 4 | BDL | 213 | 2494 | 4 | 42712 | 23463 | Normal |  | 2025 | Jul
360 | MRSS | 135MVA TR -2 | 135 | 135 | 101 to 200 | 2008363 | Power Transformer | Normal |  | 01.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 1 | 1 | BDL | 18 | 153 | 2 | 17019 | 9652 | Normal |  | 2025 | Jul
361 | MRSS | 135MVA TR -3 | 135 | 135 | 101 to 200 | 6800000138 | Power Transformer | Moderate |  | 2025-09-26 |  | NA | NA | NA | NA | NA | NA | NA | NA | 10 | 78 | 65 | 343 | 4 | 287 | 2435 | 9 | 40142 | 21366 | Moderate |  | 2025 | Sep
362 | MRSS | 135MVA TR -5 | 135 | 135 | 101 to 200 | TWBO6632/B29965 | Power Transformer | Normal |  | 14.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 2 | 2 | BDL | 676 | 2698 | 3 | 31957 | 8689 | Normal |  | 2025 | Jul
363 | MRSS | 160MVA TR -1 | 160 | 160 | 101 to 200 | TWBO6633/B3004 | Power Transformer | Normal | Normal | 05.04.2025 | 64 | 10 | 0.02 | 0.0002 | 2216 | Not detected | 38.2 | 178 | 0.827 | 9 | 15 | 11 | 45 | BDL | 499 | 3114 | 22 | 41854 | 16233 | Normal | Normal | 2025 | Apr
364 | MRSS | 160MVA TR -2 | 160 | 160 | 101 to 200 | TWBO6837/B30540 | Power Transformer | Normal |  | 05.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 12 | 3 | 1 | 1 | BDL | 219 | 805 | 2 | 34212 | 9175 | Normal |  | 2025 | Jul
365 | MRSS | 20MVA TR -1 | 20 | 20 | 11 to 20 | 2800054086 | Power Transformer | Normal |  | 14.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 2 | 3 | BDL | 162 | 3184 | 5 | 43094 | 14912 | Normal |  | 2025 | Jul
366 | MRSS | 20MVA TR -2 | 20 | 20 | 11 to 20 | 2800054085 | Power Transformer | Normal |  | 14.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 20 | 9 | 5 | 3 | BDL | 262 | 3740 | 5 | 38807 | 19572 | Normal |  | 2025 | Jul
367 | MRSS | 20MVA TR -3 | 20 | 20 | 11 to 20 | 2800055233 | Power Transformer | Normal |  | 14.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 14 | 3 | 4 | 9 | BDL | 378 | 4125 | 5 | 42352 | 21712 | Normal |  | 2025 | Jul
368 | MRSS | 2 MVA Station Trafo | 2 | 2 | 1 to 2 | 09 OG-085/01 | Power Transformer | Normal |  | 14.07.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 35 | 883 | 5 | 45567 | 29709 | Normal |  | 2025 | Jul
369 | MRSS | TR-1 | 75/90 | 75 | 51 to 100 | T-6720/B-30205 | Power Transformer | Normal | Normal | 21.08.2025 | 76 | 7 | 0.02 | 0.003 | 514 | Not detected | 42.4 | 178 | 0.827 | 7 | 6 | 3 | 9 | BDL | 704 | 2589 | 3 | 37345 | 15418 | Normal | Normal | 2025 | Aug
370 | MRSS | TR-2 | 75/90 | 75 | 51 to 100 | T-6720/B-30206 | Power Transformer | Normal | Normal | 22.08.2025 | 70 | 9 | 0.02 | 0.002 | 714 | Not detected | 42.3 | 170 | 0.822 | 7 | 13 | 4 | 7 | BDL | 616 | 2389 | 4 | 40708 | 16448 | Normal | Normal | 2025 | Aug
371 | MRSS | TR-3 | 75/90 | 75 | 51 to 100 | T-6720/B-30207 | Power Transformer | Normal | Normal | 22.08.2025 | 73 | 14 | 0.02 | 0.0004 | 1008 | Not detected | 40.9 | 176 | 0.822 | 5 | 10 | 5 | 16 | BDL | 484 | 3198 | 7 | 41811 | 16578 | Normal | Normal | 2025 | Aug
372 | MRSS | TR-4 | 130/160 | 130 | 101 to 200 | T-6719(670700179)/B-30203 | Power Transformer | Normal | Normal | 22.08.2025 | 83 | 6 | 0.02 | 0.001 | 704 | Not detected | 41.3 | 178 | 0.822 | 4 | 4 | 2 | 3 | BDL | 302 | 1131 | 3 | 24745 | 8702 | Normal | Normal | 2025 | Aug
373 | MRSS | TR-5 | 130/160 | 130 | 101 to 200 | T-6719(670700179)/B-30204 | Power Transformer | Normal | Normal | 22.08.2025 | 85 | 12 | 0.02 | 0.0004 | 1508 | Not detected | 42.7 | 176 | 0.822 | 10 | 26 | 10 | 29 | BDL | 865 | 5599 | 5 | 41789 | 8480 | Normal | Normal | 2025 | Aug
374 | MRSS | TR-6 | 130/160 | 130 | 101 to 200 | T-6787(670800395)/B30541 | Power Transformer | Normal | Normal | 22.08.2025 | 59 | 14 | 0.02 | 0.0005 | 1920 | Not detected | 42.3 | 172 | 0.822 | 11 | 7 | 4 | 10 | BDL | 552 | 4424 | 5 | 40138 | 12549 | Normal | Normal | 2025 | Aug
375 | MRSS | TR-7 | 130/160 | 130 | 101 to 200 | T-6787(670800395)/B30438 | Power Transformer | Moderate |  | 26.09.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 31 | 24 | 21 | 98 | 2 | 599 | 4912 | 5 | 38211 | 22612 | Moderate |  | 2025 | Sep
376 | MRSS | TR-8 | 165/195 | 165 | 101 to 200 | T-6788(670800396)/B30459 | Power Transformer | Moderate |  | 26.09.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 48 | 34 | 14 | 88 | 5 | 603 | 3862 | 4 | 38015 | 15162 | Moderate |  | 2025 | Sep
377 | MRSS | TR-9 | 165/195 | 165 | 101 to 200 | T-6775(670800198)/B30367 | Power Transformer | Normal | Normal | 21.08.2025 | 74 | 12 | 0.02 | 0.0007 | 1203 | Not detected | 43 | 174 | 0.827 | 21 | 3 | 3 | 6 | BDL | 246 | 1785 | 4 | 38578 | 12856 | Normal | Normal | 2025 | Aug
378 | MRSS | TR-10 | 165/195 | 165 | 101 to 200 | T-6775(670800198)/B30366 | Power Transformer | Moderate |  | 2025-09-25 |  | NA | NA | NA | NA | NA | NA | NA | NA | 20 | 133 | 39 | 352 | BDL | 376 | 3508 | 5 | 23107 | 8718 | Moderate |  | 2025 | Sep
379 | MRSS | STATION TR-1 | 1 | 1 | 1 to 2 | 07LG067/02 | Power Transformer | Moderate |  | 2025-09-25 |  | NA | NA | NA | NA | NA | NA | NA | NA | 1318 | 22 | 4 | 2 | BDL | 91 | 1425 | 4 | 52262 | 22419 | Moderate |  | 2025 | Sep
380 | MRSS | STATION TR-2 | 1 | 1 | 1 to 2 | 07LG067/01 | Power Transformer | Normal | Normal | 22.08.2025 | 53 | 19 | 0.02 | 0.0003 | 1079 | Not detected | 36.7 | 178 | 0.822 | 4 | 2 | 3 | 4 | BDL | 66 | 1232 | 4 | 39421 | 21607 | Normal | Normal | 2025 | Aug
653 | MRSS | MRSS 1 | 135 | 135 | 101 to 200 | 100MVA TR -1 | Power Transformer
654 | MRSS | MRSS 1 | 100/140 | 100 | 51 to 100 | 100MVA TR -2 | Power Transformer
655 | MRSS | MRSS 1 | 100 | 100 | 51 to 100 | 100MVA TR -3 | Power Transformer
656 | MRSS | MRSS 1 | 135 | 135 | 101 to 200 | 135MVA TR -1 | Power Transformer
657 | MRSS | MRSS 1 | 135 | 135 | 101 to 200 | 135MVA TR -2 | Power Transformer
658 | MRSS | MRSS 1 | 135 | 135 | 101 to 200 | 135MVA TR -3 | Power Transformer
659 | MRSS | MRSS 1 | 135 | 135 | 101 to 200 | 135MVA TR -5 | Power Transformer
660 | MRSS | MRSS 1 | 160 | 160 | 101 to 200 | 160MVA TR -1 | Power Transformer
661 | MRSS | MRSS 1 | 160 | 160 | 101 to 200 | 160MVA TR -2 | Power Transformer
662 | MRSS | MRSS 1 LBSS-1 | 20 | 20 | 11 to 20 | 20MVA TR -1 | Power Transformer
663 | MRSS | MRSS 1 LBSS-1 | 20 | 20 | 11 to 20 | 20MVA TR -2 | Power Transformer
664 | MRSS | MRSS 1 LBSS-1 | 20 | 20 | 11 to 20 | 20MVA TR -3 | Power Transformer
665 | MRSS | MRSS 1 SVC-3 | 2 | 2 | 1 to 2 | 2 MVA Station Trafo | Power Transformer
666 | MRSS | MRSS 2 BAY 3 | 75/90 | 75 | 51 to 100 | TR-1 | Power Transformer
667 | MRSS | MRSS 2 BAY 4 | 75/90 | 75 | 51 to 100 | TR-2 | Power Transformer
668 | MRSS | MRSS 2 BAY 5 | 75/90 | 75 | 51 to 100 | TR-3 | Power Transformer
669 | MRSS | MRSS 2 BAY 6 | 130/160 | 130 | 101 to 200 | TR-4 | Power Transformer
670 | MRSS | MRSS 2 BAY 7 | 130/160 | 130 | 101 to 200 | TR-5 | Power Transformer
671 | MRSS | MRSS 2 BAY 8 | 130/160 | 130 | 101 to 200 | TR-6 | Power Transformer
672 | MRSS | MRSS 2 BAY 9 | 130/160 | 130 | 101 to 200 | TR-7 | Power Transformer
673 | MRSS | MRSS 2 BAY 14 | 165/195 | 165 | 101 to 200 | TR-8 | Power Transformer
674 | MRSS | MRSS 2 BAY 15 | 165/195 | 165 | 101 to 200 | TR-9 | Power Transformer
675 | MRSS | MRSS 2 BAY 16 | 165/195 | 165 | 101 to 200 | TR-10 | Power Transformer
676 | MRSS | MRSS-2 SS | 1 | 1 | 1 to 2 | STATION TR-1 | Power Transformer
677 | MRSS | MRSS-2 SS | 1 | 1 | 1 to 2 | STATION TR-2 | Power Transformer
678 | MRSS | 500MW CCPP | 100 | 100 | 51 to 100 | MRSS-1 spare TR 100MVA | Power Transformer
679 | MRSS | 220 KV SWYD | 20 | 20 | 11 to 20 | MRSS-1spare TR 20MVA | Power Transformer
381 | OXYGEN PLANT | 20 MVA POWER TR-1 | 20 | 20 | 11 to 20 | 23659/1 | Power Transformer | Normal | Normal | 31.05.2025 | 60 | 14 | NA | NA | NA | NA | NA | NA | NA | 1 | 4 | 2 | 3 | BDL | 240 | 1187 | 4 | 38114 | 24852 | Normal | Normal | 2025 | May
382 | OXYGEN PLANT | PLANT-1 DISTRIBUTION TR-1 | 2 | 2 | 1 to 2 | 3055/18 | Power Transformer | Normal | Normal | 31.05.2025 | 56 | 31 | NA | NA | NA | NA | NA | NA | NA | 1 | 4 | 4 | 6 | BDL | 77 | 3138 | 7 | 41651 | 23092 | Normal | Normal | 2025 | May
383 | OXYGEN PLANT | PLANT-1 DISTRIBUTION TR-2 | 2 | 2 | 1 to 2 | 3458/1 | Power Transformer | Normal | Moderate | 31.05.2025 | 35 | 63 | NA | NA | NA | NA | NA | NA | NA | 4 | 4 | 3 | 10 | BDL | 149 | 3765 | 8 | 35588 | 24442 | Normal | Moderate | 2025 | May
384 | OXYGEN PLANT | 30 MVA POWER TR-1 | 30 | 30 | 21 to 50 | 042XG003 | Power Transformer | Normal | Normal | 31.05.2025 | 56 | 14 | NA | NA | NA | NA | NA | NA | NA | 3 | 3 | 3 | 8 | BDL | 115 | 736 | 3 | 40887 | 28068 | Normal | Normal | 2025 | May
385 | OXYGEN PLANT | PLANT-2 DISTRIBUTION TR-1 | 2 | 2 | 1 to 2 | 04OD122/01 | Power Transformer | Normal | Normal | 31.05.2025 | 58 | 28 | NA | NA | NA | NA | NA | NA | NA | 39 | 3 | 3 | 4 | BDL | 82 | 1332 | 9 | 41999 | 26805 | Normal | Normal | 2025 | May
386 | OXYGEN PLANT | PLANT-2 DISTRIBUTION TR-2 | 2 | 2 | 1 to 2 | 04OD121/01 | Power Transformer | Normal | Normal | 31.05.2025 | 59 | 23 | NA | NA | NA | NA | NA | NA | NA | 19 | 4 | 3 | 4 | BDL | 76 | 803 | 9 | 43274 | 29685 | Normal | Normal | 2025 | May
387 | OXYGEN PLANT | PLANT-2 DISTRIBUTION TR-3 | 2 | 2 | 1 to 2 | 04OD122/02 | Power Transformer | Normal | Normal | 31.05.2025 | 51 | 19 | NA | NA | NA | NA | NA | NA | NA | 9 | 3 | 3 | 4 | BDL | 40 | 1203 | 5 | 41642 | 17177 | Normal | Normal | 2025 | May
646 | OXYGEN PLANT | Oxygen plant | 20 | 20 | 11 to 20 | 20 MVA POWER TR-1 | Power Transformer
647 | OXYGEN PLANT | Oxygen plant | 2 | 2 | 1 to 2 | PLANT-1 DISTRIBUTION TR-1 | Power Transformer
648 | OXYGEN PLANT | Oxygen plant | 2 | 2 | 1 to 2 | PLANT-1 DISTRIBUTION TR-2 | Power Transformer
649 | OXYGEN PLANT | Oxygen plant | 30 | 30 | 21 to 50 | 30 MVA POWER TR-1 | Power Transformer
650 | OXYGEN PLANT | Oxygen plant | 2 | 2 | 1 to 2 | PLANT-2 DISTRIBUTION TR-1 | Power Transformer
651 | OXYGEN PLANT | Oxygen plant | 2 | 2 | 1 to 2 | PLANT-2 DISTRIBUTION TR-2 | Power Transformer
652 | OXYGEN PLANT | Oxygen plant | 2 | 2 | 1 to 2 | PLANT-2 DISTRIBUTION TR-3 | Power Transformer
388 | PIPE MILL | COATING Main 33KV Trafo. | 20/25 | 20 | 11 to 20 | 07-ZG 010-10 | Power Transformer | Normal | Normal | 05.06.2025 | 54 | 16 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 5 | 22 | BDL | 18 | 797 | 6 | 40938 | 31106 | Normal | Normal | 2025 | Jun
389 | PIPE MILL | COATING Trafo-1 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/11 | Power Transformer | Normal | Normal | 05.06.2025 | 50 | 29 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 2 | 3 | BDL | 27 | 618 | 5 | 39812 | 29647 | Normal | Normal | 2025 | Jun
390 | PIPE MILL | COATING Trafo-2 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/12 | Power Transformer | Normal | Normal | 05.06.2025 | 52 | 27 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 2 | 4 | BDL | 22 | 729 | 5 | 44996 | 33654 | Normal | Normal | 2025 | Jun
391 | PIPE MILL | COATING Trafo-3 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/13 | Power Transformer | Normal | Normal | 05.06.2025 | 52 | 22 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 2 | 3 | BDL | 13 | 577 | 5 | 41046 | 31138 | Normal | Normal | 2025 | Jun
392 | PIPE MILL | INDUCTION TR-1 | 2 | 2 | 1 to 2 | 08 COC 091/01 | Power Transformer | Normal | Normal | 05.06.2025 | 52 | 21 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 1 | 1 | BDL | 38 | 538 | 5 | 40220 | 29928 | Normal | Normal | 2025 | Jun
393 | PIPE MILL | INDUCTION TR-2 | 1.876 | 1.876 | 1 to 2 | CNC 078/01 | Power Transformer | Normal | Normal | 05.06.2025 | 52 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 2 | 3 | BDL | 13 | 356 | 5 | 42785 | 29472 | Normal | Normal | 2025 | Jun
394 | PIPE MILL | HSAW-1 TR-1 | 2.5 | 2.5 | 3 to 5 | 07PC204/14 | Power Transformer | Normal | Normal | 06.06.2025 | 56 | 22 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 39 | 644 | 5 | 38864 | 27192 | Normal | Normal | 2025 | Jun
395 | PIPE MILL | HSAW-1 TR-2 | 2.5 | 2.5 | 3 to 5 | 07PC204/06 | Power Transformer | Normal | Normal | 06.06.2025 | 55 | 19 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 34 | 481 | 5 | 38700 | 28016 | Normal | Normal | 2025 | Jun
396 | PIPE MILL | HSAW-1 TR-3 | 2.5 | 2.5 | 3 to 5 | 07PC204/08 | Power Transformer | Normal | Normal | 06.06.2025 | 60 | 18 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 3 | BDL | 37 | 497 | 4 | 40112 | 29256 | Normal | Normal | 2025 | Jun
397 | PIPE MILL | HSAW-2 TR-1 | 2.5 | 2.5 | 3 to 5 | 07PC204/07 | Power Transformer | Normal | Normal | 06.06.2025 | 51 | 25 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 7 | BDL | 35 | 757 | 7 | 39341 | 29474 | Normal | Normal | 2025 | Jun
398 | PIPE MILL | HSAW-2 TR-2 | 2.5 | 2.5 | 3 to 5 | 07PC204/05 | Power Transformer | Normal | Normal | 06.06.2025 | 65 | 10 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 3 | BDL | 49 | 452 | 5 | 42404 | 27330 | Normal | Normal | 2025 | Jun
399 | PIPE MILL | HSAW-2 TR-3 | 2.5 | 2.5 | 3 to 5 | 07PC204/13 | Power Transformer | Normal | Normal | 06.06.2025 | 55 | 22 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 3 | BDL | 45 | 862 | 5 | 40382 | 28644 | Normal | Normal | 2025 | Jun
400 | PIPE MILL | LSAW TR-1 | 2.5 | 2.5 | 3 to 5 | 09 PC-046/01 | Power Transformer | Normal | Normal | 07.06.2025 | 55 | 25 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 40 | 678 | 5 | 40727 | 29420 | Normal | Normal | 2025 | Jun
401 | PIPE MILL | LSAW TR-2 | 2.5 | 2.5 | 3 to 5 | 09 PC-046/02 | Power Transformer | Normal | Normal | 07.06.2025 | 57 | 13 | NA | NA | NA | NA | NA | NA | NA | 1 | 4 | 3 | 11 | BDL | 36 | 603 | 7 | 38068 | 27934 | Normal | Normal | 2025 | Jun
402 | PIPE MILL | LSAW TR-3 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/09 | Power Transformer | Normal | Normal | 07.06.2025 | 69 | 25 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 5 | BDL | 36 | 728 | 5 | 39708 | 27979 | Normal | Normal | 2025 | Jun
403 | PIPE MILL | LSAW TR-4 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/10 | Power Transformer | Normal | Normal | 07.06.2025 | 70 | 20 | NA | NA | NA | NA | NA | NA | NA | 4 | 3 | 3 | 3 | BDL | 35 | 571 | 5 | 38326 | 27359 | Normal | Normal | 2025 | Jun
404 | PIPE MILL | COATING TR-6 | 1.876 | 1.876 | 1 to 2 | CNC 078/01 | Power Transformer | Normal | Normal | 05.06.2025 | 52 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 2 | 3 | BDL | 13 | 356 | 5 | 42785 | 29472 | Normal | Normal | 2025 | Jun
948 | PIPE MILL | COATING | 20/25 | 20 | 11 to 20 | Main 33KV Trafo. | Power Transformer
949 | PIPE MILL | COATING | 2.5 | 2.5 | 3 to 5 | Trafo-1 | Power Transformer
950 | PIPE MILL | COATING | 2.5 | 2.5 | 3 to 5 | Trafo-2 | Power Transformer
951 | PIPE MILL | COATING | 2.5 | 2.5 | 3 to 5 | Trafo-3 | Power Transformer
952 | PIPE MILL | COATING | 2 | 2 | 1 to 2 | Trafo-4(converter duty) | Power Transformer
953 | PIPE MILL | COATING | 1.6 | 1.6 | 1 to 2 | Trafo-5(converter duty) | Power Transformer
954 | PIPE MILL | HSAW-1 | 2.5 | 2.5 | 3 to 5 | Trafo-1 | Power Transformer
955 | PIPE MILL | HSAW-1 | 2.5 | 2.5 | 3 to 5 | Trafo-2 | Power Transformer
956 | PIPE MILL | HSAW-1 | 2.5 | 2.5 | 3 to 5 | Trafo-3 | Power Transformer
957 | PIPE MILL | HSAW-2 | 2.5 | 2.5 | 3 to 5 | Trafo-1 | Power Transformer
958 | PIPE MILL | HSAW-2 | 2.5 | 2.5 | 3 to 5 | Trafo-2 | Power Transformer
959 | PIPE MILL | HSAW-2 | 2.5 | 2.5 | 3 to 5 | Trafo-3 | Power Transformer
960 | PIPE MILL | LSAW | 2.5 | 2.5 | 3 to 5 | Trafo-1 | Power Transformer
961 | PIPE MILL | LSAW | 2.5 | 2.5 | 3 to 5 | Trafo-2 | Power Transformer
962 | PIPE MILL | LSAW | 2.5 | 2.5 | 3 to 5 | Trafo-3 | Power Transformer
963 | PIPE MILL | LSAW | 2.5 | 2.5 | 3 to 5 | Trafo-4 | Power Transformer
964 | PIPE MILL | COATING | 1.876 | 1.876 | 1 to 2 | Trafo-6(converter duty) | Power Transformer
965 | PLATE MILL | ER1 | 2 | 2 | 1 to 2 | LSU-1,ER-1 | Power Transformer
966 | PLATE MILL | ER1 | 1.25 | 1.25 | 1 to 2 | LSU-2,ER-1 | Power Transformer
967 | PLATE MILL | ER1 | 2 | 2 | 1 to 2 | PCC - 1.1 | Power Transformer
968 | PLATE MILL | ER1 | 2 | 2 | 1 to 2 | PCC -1.2 | Power Transformer
969 | PLATE MILL | ER2 | 31.5 | 31.5 | 21 to 50 | 6.6 KV Line-Up - 1 | Power Transformer
970 | PLATE MILL | ER2 | 4.1 | 4.1 | 3 to 5 | MAIN DRIVE TRAFO TOP - 2.1 | Power Transformer
971 | PLATE MILL | ER2 | 4.1 | 4.1 | 3 to 5 | MAIN DRIVE TRAFO TOP - 2.2 | Power Transformer
972 | PLATE MILL | ER2 | 4.1 | 4.1 | 3 to 5 | MAIN DRIVE TRAFO TOP - 2.3 | Power Transformer
973 | PLATE MILL | ER2 | 4.1 | 4.1 | 3 to 5 | MAIN DRIVE TRAFO BOTTOM - 3.1 | Power Transformer
974 | PLATE MILL | ER2 | 4.1 | 4.1 | 3 to 5 | MAIN DRIVE TRAFO BOTTOM - 3.2 | Power Transformer
975 | PLATE MILL | ER2 | 4.1 | 4.1 | 3 to 5 | MAIN DRIVE TRAFO BOTTOM - 3.3 | Power Transformer
976 | PLATE MILL | ER2 | 1.6 | 1.6 | 1 to 2 | EXCITATION TRANFO | Power Transformer
977 | PLATE MILL | ER2 | 2 | 2 | 1 to 2 | LSU-1,ER-2 | Power Transformer
978 | PLATE MILL | ER2 | 2.5 | 2.5 | 3 to 5 | LSU-2,ER-2 | Power Transformer
979 | PLATE MILL | ER2 | 2.5 | 2.5 | 3 to 5 | LSU-3,ER-2 | Power Transformer
980 | PLATE MILL | ER2 | 1.25 | 1.25 | 1 to 2 | LSU-4,ER-2 | Power Transformer
981 | PLATE MILL | ER2 | 2 | 2 | 1 to 2 | PCC 2.1 | Power Transformer
982 | PLATE MILL | ER2 | 2 | 2 | 1 to 2 | PCC 2.2 | Power Transformer
983 | PLATE MILL | ER3 | 31.5 | 31.5 | 21 to 50 | 6.6 KV Line-Up - 2 | Power Transformer
984 | PLATE MILL | ER3 | 1.6 | 1.6 | 1 to 2 | LSU-1,ER-3 | Power Transformer
985 | PLATE MILL | ER3 | 2 | 2 | 1 to 2 | LSU-2,ER-3 | Power Transformer
986 | PLATE MILL | ER3 | 1.25 | 1.25 | 1 to 2 | LSU-3,ER-3 | Power Transformer
987 | PLATE MILL | ER3 | 1.25 | 1.25 | 1 to 2 | LSU-4,ER-3 | Power Transformer
988 | PLATE MILL | ER3 | 2 | 2 | 1 to 2 | PCC - 3.1 | Power Transformer
989 | PLATE MILL | ER3 | 2 | 2 | 1 to 2 | PCC - 3.2 | Power Transformer
990 | PLATE MILL | ER3 | 2 | 2 | 1 to 2 | PCC - 3.3 | Power Transformer
991 | PLATE MILL | ER3 | 2 | 2 | 1 to 2 | PCC - 3.4 | Power Transformer
992 | PLATE MILL | ER4 | 1.6 | 1.6 | 1 to 2 | LSU-1,ER-4 | Power Transformer
993 | PLATE MILL | ER4 | 2 | 2 | 1 to 2 | LSU-2,ER-4 | Power Transformer
994 | PLATE MILL | ER4 | 2 | 2 | 1 to 2 | PCC - 4.1 | Power Transformer
995 | PLATE MILL | ER5 | 2 | 2 | 1 to 2 | LSU-1,ER-5 | Power Transformer
996 | PLATE MILL | ER5 | 2.5 | 2.5 | 3 to 5 | LSU-2,ER-5 | Power Transformer
997 | PLATE MILL | ER5 | 2 | 2 | 1 to 2 | LSU-3,ER-5 | Power Transformer
998 | PLATE MILL | ER5 | 3.5 | 3.5 | 3 to 5 | LSU-4,ER-5 | Power Transformer
999 | PLATE MILL | ER5 | 2 | 2 | 1 to 2 | PCC - 5.1 | Power Transformer
1000 | PLATE MILL | ER6 | 1.25 | 1.25 | 1 to 2 | LSU-1,ER-6 | Power Transformer
1001 | PLATE MILL | ER6 | 2 | 2 | 1 to 2 | LSU-2,ER-6 | Power Transformer
1002 | PLATE MILL | ER6 | 2.25 | 2.25 | 3 to 5 | LSU-3 Heat Treatment | Power Transformer
1003 | PLATE MILL | ER6 | 2 | 2 | 1 to 2 | PCC - 6.1 | Power Transformer
1004 | PLATE MILL | ER6 | 2 | 2 | 1 to 2 | PCC - 6.2 | Power Transformer
1005 | PLATE MILL | ER6 | 2 | 2 | 1 to 2 | PCC - 6.3 | Power Transformer
1006 | PLATE MILL | ER6 | 2 | 2 | 1 to 2 | PCC-6.4 | Power Transformer
1007 | PLATE MILL | ER7 | 2 | 2 | 1 to 2 | PCC - 7.1 | Power Transformer
1008 | PLATE MILL | ER7 | 2 | 2 | 1 to 2 | PCC - 7.2 | Power Transformer
1009 | PLATE MILL | ER7 | 2 | 2 | 1 to 2 | PCC - 7.3 | Power Transformer
1010 | PLATE MILL | Slab Yard | 4.1 | 4.1 | 3 to 5 | Spare (main drive trafo#1) | Power Transformer
1011 | PLATE MILL | Slab Yard | 4.1 | 4.1 | 3 to 5 | Spare (main drive trafo#2) | Power Transformer
1012 | PLATE MILL | Slab Yard | 4.1 | 4.1 | 3 to 5 | Spare (main drive trafo#3) | Power Transformer
1013 | PLATE MILL | Slab Yard | 1.6 | 1.6 | 1 to 2 | Spare (main drive excitation) | Power Transformer
405 | Power Infra | 25 MVA Trafo-1 | 25 | 25 | 21 to 50 | 09 ZD 001 | Power Transformer | Normal | Normal | 17.09.2025 | 62 | 21 | 0.01 | 0.001 | 426 | Not detected | 31.3 | 166 | 0.822 | 2 | 2 | 4 | 7 | BDL | 643 | 8136 | 5 | 47252 | 14854 | Normal | Normal | 2025 | Sep
406 | Power Infra | 25 MVA Trafo-2 | 25 | 25 | 21 to 50 | M147 | Power Transformer | Normal | Normal | 17.09.2025 | 69 | 30 | 0.02 | 0.002 | 480 | Not detected | 31.6 | 178 | 0.822 | 10 | 2 | 8 | 26 | BDL | 104 | 3532 | 4 | 39762 | 21892 | Normal | Normal | 2025 | Sep
407 | Power Infra | Boiler-Trf-1 | 2 | 2 | 1 to 2 | 08-OC-094/08 | Power Transformer | Normal | Normal | 17.09.2025 | 52 | 12 | 0.02 | 0.001 | 2268 | Not detected | 32 | 162 | 0.822 | 7 | 2 | 3 | 3 | BDL | 39 | 1326 | 7 | 43758 | 32652 | Normal | Normal | 2025 | Sep
408 | Power Infra | Boiler-Trf-2 | 2 | 2 | 1 to 2 | 08-OC-094/07 | Power Transformer | Normal | Normal | 17.09.2025 | 65 | 21 | 0.02 | 0.001 | 1536 | Not detected | 33.4 | 462 | 0.822 | 2 | 2 | 3 | 4 | BDL | 50 | 2303 | 5 | 43678 | 32162 | Normal | Normal | 2025 | Sep
641 | POWER INFRA | 19MW PP | 25 | 25 | 21 to 50 | 25 MVA Trafo | Power Transformer
642 | POWER INFRA | 19MW PP | 25 | 25 | 21 to 50 | 25MVA | Power Transformer
643 | POWER INFRA | BOILER AREA | 2 | 2 | 1 to 2 | Boiler-Trf-1 | Power Transformer
644 | POWER INFRA | BOILER AREA | 2 | 2 | 1 to 2 | Boiler-Trf-2 | Power Transformer
645 | POWER INFRA | 515MW PP | 12.5 | 12.5 | 11 to 20 | 12.5MVA Trafo | Power Transformer
1187 | SERVICE CENTRE - HAZ | PSL-2 | 2 | 2 | 1 to 2 | PSL-2 DISTRIBUTION | Power Transformer
409 | SINTER | LCSS-1 TR-1 | 15/21 | 15 | 11 to 20 | 93026 | Power Transformer | Normal | Normal | 04.08.2025 | 38 | 35 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 2 | 3 | BDL | 90 | 2112 | 4 | 42476 | 19974 | Normal | Normal | 2025 | Aug
410 | SINTER | LCSS-1 TR-2 | 15/21 | 15 | 11 to 20 | MT8292/U1 | Power Transformer | Normal | Normal | 04.08.2025 | 56 | 19 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 2 | 3 | BDL | 159 | 4792 | 5 | 41755 | 21706 | Normal | Normal | 2025 | Aug
411 | SINTER | LCSS-1 TR-3 | 6.3 | 6.3 | 6 to 10 | S0-20-1506 | Power Transformer | Normal | Normal | 04.08.2025 | 59 | 16 | NA | NA | NA | NA | NA | NA | NA | 19 | 2 | 2 | 3 | BDL | 327 | 3670 | 4 | 40348 | 22691 | Normal | Normal | 2025 | Aug
412 | SINTER | LCSS-1 TR-4 | 0.5 | 0.5 | 0 - 0.9 | V-362 | Distribution Transformer | Normal | Normal | 04.08.2025 | 47 | 28 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 1 | 3 | BDL | 93 | 1676 | 4 | 44716 | 22925 | Normal | Normal | 2025 | Aug
413 | SINTER | LCSS-1 TR-5 | 3.5 | 3.5 | 3 to 5 | 3/GH073 | Power Transformer | Normal | Normal | 05.08.2025 | 47 | 33 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 48 | 1400 | 4 | 41249 | 22748 | Normal | Normal | 2025 | Aug
414 | SINTER | LCSS-1 TR-6 | 3.5 | 3.5 | 3 to 5 | 8/GH073 | Power Transformer | Normal | Normal | 05.08.2025 | 42 | 29 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 36 | 1003 | 4 | 43523 | 21467 | Normal | Normal | 2025 | Aug
415 | SINTER | LCSS-1 TR-8 | 3.5 | 3.5 | 3 to 5 | DT7707 | Power Transformer | Normal | Normal | 05.08.2025 | 54 | 12 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 68 | 1128 | 6 | 41782 | 21454 | Normal | Normal | 2025 | Aug
416 | SINTER | LCSS-2 TR-1 | 0.75 | 0.75 | 0 - 0.9 | 72109 | Distribution Transformer | Normal | Normal | 06.08.2025 | 59 | 18 | NA | NA | NA | NA | NA | NA | NA | 13 | 2 | 3 | 6 | BDL | 66 | 1236 | 4 | 40767 | 23170 | Normal | Normal | 2025 | Aug
417 | SINTER | LCSS-2 TR-2 | 0.8 | 0.8 | 0 - 0.9 | DT8056/01 | Distribution Transformer | Normal | Normal | 06.08.2025 | 57 | 29 | NA | NA | NA | NA | NA | NA | NA | 34 | 2 | 3 | 3 | BDL | 82 | 2756 | 4 | 42080 | 23742 | Normal | Normal | 2025 | Aug
418 | SINTER | LCSS-2 TR-3 | 0.75 | 0.75 | 0 - 0.9 | 70545 | Distribution Transformer | Normal | Normal | 07.08.2025 | 70 | 9 | NA | NA | NA | NA | NA | NA | NA | 11 | 2 | 3 | 6 | BDL | 118 | 751 | 5 | 40142 | 24857 | Normal | Normal | 2025 | Aug
419 | SINTER | LCSS-2 TR-4 | 0.75 | 0.75 | 0 - 0.9 | 72105 | Distribution Transformer | Moderate | Normal | 07.08.2025 | 72 | 16 | NA | NA | NA | NA | NA | NA | NA | 49 | 22 | 14 | 107 | 4 | 103 | 1603 | 5 | 39412 | 22916 | Moderate | Normal | 2025 | Aug
420 | SINTER | LCSS-2 TR-5 | 0.75 | 0.75 | 0 - 0.9 | 70303 | Distribution Transformer | Normal | Normal | 07.08.2025 | 66 | 17 | NA | NA | NA | NA | NA | NA | NA | 12 | 2 | 3 | 3 | BDL | 69 | 1663 | 4 | 44716 | 21936 | Normal | Normal | 2025 | Aug
421 | SINTER | LCSS-2 TR-6 | 0.75 | 0.75 | 0 - 0.9 | 71883 | Distribution Transformer | Normal | Normal | 07.08.2025 | 69 | 16 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 102 | 2153 | 5 | 45885 | 21951 | Normal | Normal | 2025 | Aug
422 | SINTER | LCSS-3 TR-1 | 3.5 | 3.5 | 3 to 5 | 2026 | Power Transformer | Normal | Normal | 07.08.2025 | 58 | 31 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 53 | 1024 | 5 | 42777 | 21059 | Normal | Normal | 2025 | Aug
423 | SINTER | LCSS-3 TR-2 | 0.75 | 0.75 | 0 - 0.9 | 70833 | Distribution Transformer | Normal | Normal | 07.08.2025 | 67 | 25 | NA | NA | NA | NA | NA | NA | NA | 10 | 2 | 3 | 6 | BDL | 74 | 1237 | 6 | 40142 | 22457 | Normal | Normal | 2025 | Aug
424 | SINTER | LCSS-4 TR-1 | 2.5 | 2.5 | 3 to 5 | '19-01-2132 | Power Transformer | Normal | Normal | 07.08.2025 | 62 | 12 | NA | NA | NA | NA | NA | NA | NA | 17 | 2 | 4 | 6 | BDL | 211 | 2191 | 4 | 44716 | 21933 | Normal | Normal | 2025 | Aug
425 | SINTER | LCSS-4 TR-2 | 2.5 | 2.5 | 3 to 5 | 53219 | Power Transformer | Normal | Normal | 07.08.2025 | 68 | 10 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 100 | 2188 | 5 | 43393 | 23271 | Normal | Normal | 2025 | Aug
426 | SINTER | LCSS-4 TR-3 | 1 | 1 | 1 to 2 | DT7706 | Power Transformer | Normal | Normal | 08.08.2025 | 73 | 21 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 3 | 3 | BDL | 57 | 1043 | 4 | 48271 | 25198 | Normal | Normal | 2025 | Aug
427 | SINTER | OLD DE DUST ESP TR-1 | 0.099 | 0.099 | 0 - 0.9 | 3430-TR-0316-2126 | Distribution Transformer | Normal | Normal | 04.09.2025 | 65 | 19 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 2 | 3 | BDL | 46 | 1338 | 5 | 42543 | 21725 | Normal | Normal | 2025 | Sep
428 | SINTER | OLD DE DUST ESP TR-2 | 0.099 | 0.099 | 0 - 0.9 | 3430-TR-0316-2127 | Distribution Transformer | Normal | Normal | 04.09.2025 | 59 | 25 | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 2 | 2 | BDL | 35 | 1266 | 4 | 38720 | 23432 | Normal | Normal | 2025 | Sep
429 | SINTER | OLD DE DUST ESP TR-3 | 0.099 | 0.099 | 0 - 0.9 | 3430-TR-0316-2128 | Distribution Transformer | Normal | Normal | 04.09.2025 | 55 | 38 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 3 | BDL | 27 | 1060 | 5 | 39216 | 24520 | Normal | Normal | 2025 | Sep
430 | SINTER | NEW DE DUST ESP-1 | 0.099 | 0.099 | 0 - 0.9 | 3430-TR-0316-2129 | Distribution Transformer | Normal | Normal | 04.09.2025 | 57 | 13 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 3 | BDL | 23 | 794 | 5 | 39544 | 25430 | Normal | Normal | 2025 | Sep
431 | SINTER | NEW DE DUST ESP-2 | 0.099 | 0.099 | 0 - 0.9 | 3430-TR-0316-2130 | Distribution Transformer | Normal | Normal | 04.09.2025 | 57 | 19 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 2 | 3 | BDL | 100 | 2345 | 9 | 48271 | 25198 | Normal | Normal | 2025 | Sep
432 | SINTER | NEW DE DUST ESP-3 | 0.099 | 0.099 | 0 - 0.9 | 3430-TR-0316-2131 | Distribution Transformer | Normal | Normal | 04.09.2025 | 67 | 39 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 2 | 3 | BDL | 90 | 1996 | 4 | 38712 | 24510 | Normal | Normal | 2025 | Sep
433 | SINTER | NEW WESP-1 | 0.119 | 0.119 | 0 - 0.9 | 19426-01-10-2021 | Distribution Transformer | Normal | Normal | 09.09.2025 | 56 | 18 | NA | NA | NA | NA | NA | NA | NA | 52 | 2 | 2 | 2 | BDL | 137 | 1209 | 3 | 38612 | 21504 | Normal | Normal | 2025 | Sep
434 | SINTER | NEW WESP-2 | 0.073 | 0.073 | 0 - 0.9 | 100347 | Distribution Transformer | Moderate | Normal | 09.09.2025 | 51 | 17 | NA | NA | NA | NA | NA | NA | NA | 209 | 2 | 1 | 2 | BDL | 161 | 1571 | 2 | 33897 | 13620 | Moderate | Normal | 2025 | Sep
435 | SINTER | NEW WESP-3 | 0.073 | 0.073 | 0 - 0.9 | 100348 | Distribution Transformer | Moderate | Normal | 09.09.2025 | 67 | 9 | NA | NA | NA | NA | NA | NA | NA | 332 | 114 | 24 | 173 | 8 | 104 | 1286 | 3 | 29353 | 12437 | Moderate | Normal | 2025 | Sep
436 | SINTER | NEW WESP-4 | 0.073 | 0.073 | 0 - 0.9 | 100349 | Distribution Transformer | Moderate | Normal | 10.02.2025 | 76 | 16 | 0.02 | 0.002 | 1896 | Not detected | 42.5 | 160 | 0.852 | 137 | 12 | 4 | 24 | 218 | 58 | 611 | 9 | 40544 | 23299 | Moderate | Normal | 2025 | Feb
680 | SINTER PLANT | LCSS-1 | 15/21 | 15 | 11 to 20 | TRAFO-1 | Power Transformer
681 | SINTER PLANT | LCSS-1 | 15/21 | 15 | 11 to 20 | TRAFO-2 | Power Transformer
682 | SINTER PLANT | LCSS-1 | 6.3 | 6.3 | 6 to 10 | TRAFO-3 | Power Transformer
683 | SINTER PLANT | LCSS-1 | 0.5 | 0.5 | 0 - 0.9 | TRAFO-4 | Distribution Transformer
684 | SINTER PLANT | LCSS-1 | 3.5 | 3.5 | 3 to 5 | TRAFO-5 | Power Transformer
685 | SINTER PLANT | LCSS-1 | 3.5 | 3.5 | 3 to 5 | TRAFO-6 | Power Transformer
686 | SINTER PLANT | LCSS-1 | 3.5 | 3.5 | 3 to 5 | TRAFO-7 | Power Transformer
687 | SINTER PLANT | LCSS-1 | 3.5 | 3.5 | 3 to 5 | TRAFO-8 | Power Transformer
688 | SINTER PLANT | LCSS-2 | 0.75 | 0.75 | 0 - 0.9 | TRAFO-1 | Distribution Transformer
689 | SINTER PLANT | LCSS-2 | 0.8 | 0.8 | 0 - 0.9 | TRAFO-2 | Distribution Transformer
690 | SINTER PLANT | LCSS-2 | 0.75 | 0.75 | 0 - 0.9 | TRAFO-3 | Distribution Transformer
691 | SINTER PLANT | LCSS-2 | 0.75 | 0.75 | 0 - 0.9 | TRAFO-4 | Distribution Transformer
692 | SINTER PLANT | LCSS-2 | 0.75 | 0.75 | 0 - 0.9 | TRAFO-5 | Distribution Transformer
693 | SINTER PLANT | LCSS-2 | 0.75 | 0.75 | 0 - 0.9 | TRAFO-6 | Distribution Transformer
694 | SINTER PLANT | LCSS-3 | 3.5 | 3.5 | 3 to 5 | TRAFO-1 | Power Transformer
695 | SINTER PLANT | LCSS-3 | 0.75 | 0.75 | 0 - 0.9 | TRAFO-2 | Distribution Transformer
696 | SINTER PLANT | WESP | 0.07 | 0.07 | 0 - 0.9 | TRAFO-1 | Distribution Transformer
697 | SINTER PLANT | WESP | 0.07 | 0.07 | 0 - 0.9 | TRAFO-2 | Distribution Transformer
698 | SINTER PLANT | WESP | 0.07 | 0.07 | 0 - 0.9 | TRAFO-3 | Distribution Transformer
699 | SINTER PLANT | WESP | 0.07 | 0.07 | 0 - 0.9 | TRAFO-4 | Distribution Transformer
700 | SINTER PLANT | OLD DE DUST ESP | 0.099 | 0.099 | 0 - 0.9 | TRAFO-1 | Distribution Transformer
701 | SINTER PLANT | OLD DE DUST ESP | 0.099 | 0.099 | 0 - 0.9 | TRAFO-2 | Distribution Transformer
702 | SINTER PLANT | OLD DE DUST ESP | 0.099 | 0.099 | 0 - 0.9 | TRAFO-3 | Distribution Transformer
703 | SINTER PLANT | NEW DE DUST ESP | 0.099 | 0.099 | 0 - 0.9 | TRAFO-1 | Distribution Transformer
704 | SINTER PLANT | NEW DE DUST ESP | 0.099 | 0.099 | 0 - 0.9 | TRAFO-2 | Distribution Transformer
705 | SINTER PLANT | NEW DE DUST ESP | 0.099 | 0.099 | 0 - 0.9 | TRAFO-3 | Distribution Transformer
706 | SINTER PLANT | LCSS-4 | 2.5 | 2.5 | 3 to 5 | TRAFO-1 | Power Transformer
707 | SINTER PLANT | LCSS-4 | 2.5 | 2.5 | 3 to 5 | TRAFO-2 | Power Transformer
708 | SINTER PLANT | LCSS-4 | 1 | 1 | 1 to 2 | TRAFO-3 | Power Transformer
709 | SINTER PLANT | NEW WESP | 0.119 | 0.119 | 0 - 0.9 | TRAFO-1 | Distribution Transformer
710 | SINTER PLANT | NEW WESP | 39 | 39 | 21 to 50 | TRAFO-2 | Power Transformer
711 | SINTER PLANT | NEW WESP | 39 | 39 | 21 to 50 | TRAFO-3 | Power Transformer
712 | SINTER PLANT | NEW WESP | 39 | 39 | 21 to 50 | TRAFO-4 | Power Transformer
713 | SINTER PLANT | NEAR PRODUCT BUILDING | 0.75 | 0.75 | 0 - 0.9 | SPARE | Distribution Transformer
437 | SMP-1 | EAF1 HO1 | 80 | 80 | 51 to 100 | 32890 | Power Transformer | Moderate | Normal | 01.06.2025 | 53 | 29 | 0.02 | 0.001 | 233 | Not detected | 36.4 | 158 | 0.832 | 10 | 56 | 22 | 92 | BDL | 779 | 5882 | 36 | 41477 | 11370 | Moderate | Normal | 2025 | Jun
438 | SMP-1 | EAF1 HO2 | 80 | 80 | 51 to 100 | 32888 | Power Transformer | Normal |  | 06.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 4 | 7 | BDL | 382 | 3189 | 5 | 40632 | 13251 | Normal |  | 2025 | Mar
439 | SMP-1 | EAF2 HO1 | 80 | 80 | 51 to 100 | 32885 | Power Transformer | Normal |  | 06.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 9 | 2 | 3 | 4 | BDL | 652 | 4189 | 12 | 45675 | 12570 | Normal |  | 2025 | Mar
440 | SMP-1 | EAF2 HO2 | 80 | 80 | 51 to 100 | 160145 | Power Transformer | Normal |  | 06.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 4 | 47 | 38 | 3 | BDL | 298 | 4492 | 4 | 7227 | 9928 | Normal |  | 2025 | Mar
441 | SMP-1 | EAF3 HO1 | 80 | 80 | 51 to 100 | 32887 | Power Transformer | Moderate |  | 07.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 33 | 34 | 12 | 94 | 4 | 554 | 4155 | 17 | 36485 | 19517 | Moderate |  | 2025 | Mar
442 | SMP-1 | EAF3-HO2 | 80 | 80 | 51 to 100 | 32886 | Power Transformer | Normal |  | 07.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 44 | 3 | 13 | BDL | 585 | 3652 | 8 | 13804 | 18697 | Normal |  | 2025 | Mar
443 | SMP-1 | EAF4 HO1 | 100 | 100 | 51 to 100 | 160141 | Power Transformer | Normal |  | 07.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 9 | 4 | 3 | 3 | BDL | 360 | 2663 | 5 | 39806 | 23884 | Normal |  | 2025 | Mar
444 | SMP-1 | EAF4 HO2 | 101 | 101 | 101 to 200 | 101142 | Power Transformer | Normal |  | 07.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 31 | 4 | 2 | 3 | BDL | 67 | 661 | 3 | 35728 | 18592 | Normal |  | 2025 | Mar
445 | SMP-1 | LF1 | 28 | 28 | 21 to 50 | 65564 | Power Transformer | Normal |  | 08.03.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 2 | 5 | 3 | 6 | 2 | 28 | 952 | 5 | 36921 | 28474 | Normal |  | 2025 | Mar
446 | SMP-1 | LF-2 | 28 | 28 | 21 to 50 | 65801 | Power Transformer | Normal | Normal | 04.06.2025 | 51 | 36 | 0.02 | 0.001 | 480 | Not detected | 39.9 | 164 | 0.832 | 2 | 3 | 1 | 2 | BDL | 82 | 666 | 4 | 31974 | 23265 | Normal | Normal | 2025 | Jun
447 | SMP-1 | LF-3 | 28 | 28 | 21 to 50 | 64715 | Power Transformer | Normal | Normal | 04.06.2025 | 56 | 34 | 0.02 | 0.0001 | 439 | Not detected | 38 | 170 | 0.832 | 3 | 4 | 2 | 5 | BDL | 122 | 1912 | 4 | 44187 | 29826 | Normal | Normal | 2025 | Jun
448 | SMP-1 | LF-4 | 30 | 30 | 21 to 50 | 65678 | Power Transformer | Normal | Normal | 04.06.2025 | 65 | 19 | 0.02 | 0.001 | 583 | Not detected | 38.1 | 168 | 0.832 | 2 | 4 | 2 | 3 | BDL | 85 | 717 | 5 | 46641 | 28804 | Normal | Normal | 2025 | Jun
449 | SMP-1 | LF-5 | 28 | 28 | 21 to 50 | 64565 | Power Transformer | Normal | Normal | 04.06.2025 | 56 | 29 | 0.02 | 0.001 | 516 | Not detected | 37.6 | 162 | 0.832 | 5 | 6 | 3 | 10 | 2 | 108 | 1195 | 6 | 38686 | 27987 | Normal | Normal | 2025 | Jun
450 | SMP-1 | LCSS1 CRANE TR2 | 2.5 | 2.5 | 3 to 5 | 65771/1 | Power Transformer | Normal | Moderate | 03.09.2025 | 50 | 44 | 0.04 | 0.002 | 186 | Not detected | 29.5 | 172 | 0.837 | 2 | 3 | 4 | 7 | BDL | 237 | 4854 | 5 | 41217 | 22431 | Normal | Moderate | 2025 | Sep
451 | SMP-1 | LCSS-1 CASTER-1 TR-1 | 2 | 2 | 1 to 2 | 3055/4 | Power Transformer | Normal | Normal | 12.09.2025 | 45 | 39 | 0.02 | 0.003 | 111 | Not detected | 39.5 | 166 | 0.832 | 2 | 2 | 3 | 7 | BDL | 147 | 5315 | 4 | 38254 | 22451 | Normal | Normal | 2025 | Sep
452 | SMP-1 | LCSS-1 CASTER-1 TR-2 | 2 | 2 | 1 to 2 | 3055/7 | Power Transformer | Normal | Normal | 12.09.2025 | 41 | 33 | 0.02 | 0.002 | 325 | Not detected | 31.7 | 166 | 0.832 | 3 | 2 | 6 | 9 | BDL | 197 | 7065 | 5 | 40292 | 24932 | Normal | Normal | 2025 | Sep
453 | SMP-1 | LCSS-1 CASTER-1 TR-3 | 2 | 2 | 1 to 2 | 3055/9 | Power Transformer | Normal | Moderate | 12.09.2025 | 54 | 42 | 0.02 | 0.002 | 176 | Not detected | 31 | 162 | 0.832 | 2 | 1 | 4 | 6 | BDL | 110 | 8959 | 4 | 41254 | 25625 | Normal | Moderate | 2025 | Sep
454 | SMP-1 | LCSS1 EAF/LF T1 | 2 | 2 | 1 to 2 | 13771 | Power Transformer | Normal | Moderate | 03.09.2025 | 53 | 42 | 0.04 | 0.001 | 2227 | Not detected | 38.7 | 176 | 0.837 | 1 | 4 | 4 | 6 | BDL | 110 | 4907 | 4 | 41226 | 22623 | Normal | Moderate | 2025 | Sep
455 | SMP-1 | LCSS1 EAF/LF T2 | 2 | 2 | 1 to 2 | 3055/8 | Power Transformer | Normal | Moderate | 03.09.2025 | 49 | 42 | 0.04 | 0.002 | 156 | Not detected | 30.7 | 178 | 0.837 | 1 | 3 | 3 | 4 | BDL | 122 | 3595 | 4 | 41745 | 22682 | Normal | Moderate | 2025 | Sep
456 | SMP-1 | LCSS-1B TRAFO-1 | 2 | 2 | 1 to 2 | 3291/1 | Power Transformer | Normal | Moderate | 01.09.2025 | 44 | 44 | 0.04 | 0.005 | 26 | Not detected | 21.1 | 178 | 0.842 | 8 | 2 | 2 | 3 | BDL | 56 | 1481 | 4 | 42077 | 22381 | Normal | Moderate | 2025 | Sep
457 | SMP-1 | LCSS-1B TRAFO-2 | 2 | 2 | 1 to 2 | 3291/3 | Power Transformer | Normal | Moderate | 03.09.2025 | 46 | 42 | 0.04 | 0.007 | 26 | Not detected | 26.4 | 176 | 0.852 | 1 | 3 | 3 | 4 | BDL | 52 | 1406 | 5 | 41305 | 22364 | Normal | Moderate | 2025 | Sep
458 | SMP-1 | LCSS-1B TRAFO-3 | 2 | 2 | 1 to 2 | 3582 | Power Transformer | Normal | Normal | 01.09.2025 | 60 | 23 | 0.03 | 0.0007 | 1067 | Not detected | 36.5 | 172 | 0.842 | 3 | 2 | 2 | 3 | BDL | 154 | 4384 | 4 | 40945 | 20988 | Normal | Normal | 2025 | Sep
459 | SMP-1 | LCSS-5 TRAFO-1 | 2 | 2 | 1 to 2 | 6285 | Power Transformer | Normal | Normal | 01.09.2025 | 65 | 15 | 0.02 | 0.0007 | 2358 | Not detected | 36.8 | 178 | 0.822 | 4 | 1 | 4 | 7 | BDL | 59 | 1924 | 5 | 41915 | 21678 | Normal | Normal | 2025 | Sep
460 | SMP-1 | LCSS-5 TRAFO-2 | 2 | 2 | 1 to 2 | 6283 | Power Transformer | Normal | Normal | 01.09.2025 | 62 | 17 | 0.02 | 0.0005 | 1598 | Not detected | 35.3 | 178 | 0.827 | 1 | 1 | 4 | 7 | BDL | 63 | 2122 | 5 | 41689 | 24725 | Normal | Normal | 2025 | Sep
461 | SMP-1 | LCSS-5 TRAFO-3 | 2 | 2 | 1 to 2 | 6284 | Power Transformer | Normal | Normal | 03.09.2025 | 53 | 20 | 0.02 | 0.0007 | 1189 | Not detected | 34.7 | 178 | 0.822 | 2 | 2 | 3 | 3 | BDL | 47 | 1600 | 4 | 41942 | 22046 | Normal | Normal | 2025 | Sep
462 | SMP-1 | FES 1&2 | 2 | 2 | 1 to 2 | 3055/2 | Power Transformer | Normal | Normal | 25.08.2025 | 48 | 34 | 0.03 | 0.003 | 119 | Not detected | 22.8 | 172 | 0.842 | 1 | 2 | 3 | 5 | BDL | 46 | 2089 | 4 | 41128 | 22620 | Normal | Normal | 2025 | Aug
463 | SMP-1 | FE3 TRAF | 2 | 2 | 1 to 2 | 3055/14 | Power Transformer | Normal | Normal | 25.08.2025 | 48 | 30 | 0.03 | 0.004 | 937 | Not detected | 36.9 | 170 | 0.842 | 3 | 2 | 2 | 3 | BDL | 39 | 970 | 4 | 42854 | 21754 | Normal | Normal | 2025 | Aug
464 | SMP-1 | FES 2B | 2 | 2 | 1 to 2 | 3433/1 | Power Transformer | Normal | Normal | 25.08.2025 | 60 | 12 | 0.02 | 0.002 | 581 | Not detected | 23.5 | 168 | 0.842 | 11 | 2 | 3 | 4 | BDL | 84 | 1290 | 4 | 42103 | 23180 | Normal | Normal | 2025 | Aug
465 | SMP-1 | FES-STEP6-TRAF2 | 2.5 | 2.5 | 3 to 5 | 09 PC-049/01 | Power Transformer | Normal | Normal | 25.08.2025 | 60 | 6 | 0.02 | 0.002 | 733 | Not detected | 38.9 | 174 | 0.832 | 10 | 2 | 2 | 2 | BDL | 172 | 967 | 4 | 48295 | 24678 | Normal | Normal | 2025 | Aug
466 | SMP-1 | LIME TR-1 | 2 | 2 | 1 to 2 | 3055/13 | Power Transformer | Normal | Normal | 27.08.2025 | 51 | 21 | 0.02 | 0.0009 | 859 | Not detected | 35.1 | 178 | 0.832 | 4 | 2 | 3 | 4 | BDL | 275 | 7629 | 4 | 38254 | 22451 | Normal | Normal | 2025 | Aug
467 | SMP-1 | LIME TR-2 | 2 | 2 | 1 to 2 | 3582 | Power Transformer | Normal | Normal | 27.08.2025 | 46 | 33 | 0.03 | 0.002 | 191 | Not detected | 25.2 | 178 | 0.832 | 1 | 2 | 2 | 3 | BDL | 88 | 2474 | 4 | 39421 | 21607 | Normal | Normal | 2025 | Aug
468 | SMP-1 | LIME TR-3 | 2 | 2 | 1 to 2 | 030C-042/03 | Power Transformer | Normal | Normal | 27.08.2025 | 55 | 14 | 0.02 | 0.001 | 1466 | Not detected | 39.5 | 176 | 0.827 | 14 | 2 | 3 | 4 | BDL | 337 | 2868 | 4 | 38952 | 21547 | Normal | Normal | 2025 | Aug
469 | SMP-1 | LIME TR-4 | 2 | 2 | 1 to 2 | 030C-042/04 | Power Transformer | Normal | Normal | 27.08.2025 | 56 | 22 | 0.02 | 0.004 | 147 | Not detected | 30.6 | 170 | 0.827 | 9 | 2 | 3 | 4 | BDL | 264 | 2623 | 6 | 39824 | 20587 | Normal | Normal | 2025 | Aug
470 | SMP-1 | CASTER-2 TRAFO1 | 2 | 2 | 1 to 2 | 03OC42/02 | Power Transformer | Normal | Normal | 12.09.2025 | 57 | 18 | 0.02 | 0.002 | 333 | Not detected | 32.3 | 172 | 0.837 | 2 | 1 | 3 | 3 | BDL | 64 | 1321 | 4 | 41617 | 24048 | Normal | Normal | 2025 | Sep
471 | SMP-1 | CASTER-2 TRAFO2 | 2 | 2 | 1 to 2 | 03OC42/01 | Power Transformer | Normal | Normal | 13.09.2025 | 70 | 15 | 0.02 | 0.002 | 623 | Not detected | 34.6 | 172 | 0.837 | 7 | 2 | 2 | 2 | BDL | 97 | 1053 | 4 | 41854 | 20522 | Normal | Normal | 2025 | Sep
472 | SMP-1 | CASTER-3 TRAFO1 | 2 | 2 | 1 to 2 | 3291/4 | Power Transformer | Normal | Moderate | 13.09.2025 | 44 | 42 | 0.02 | 0.002 | 459 | Not detected | 33.2 | 162 | 0.837 | 1 | 2 | 3 | 6 | BDL | 120 | 5792 | 5 | 42154 | 26532 | Normal | Moderate | 2025 | Sep
473 | SMP-1 | CASTER-3 TRAFO2 | 2 | 2 | 1 to 2 | 3433/2 | Power Transformer | Normal | Normal | 13.09.2025 | 48 | 35 | 0.02 | 0.0001 | 464 | Not detected | 33.7 | 172 | 0.837 | 1 | 1 | 3 | 1 | BDL | 62 | 3617 | 6 | 41854 | 26054 | Normal | Normal | 2025 | Sep
789 | SMP-1 | SMP-1 | 2x40.065 | 80.13 | 51 to 100 | EAF1 HO1 | Power Transformer
790 | SMP-1 | SMP-1 | 2x40.065 | 80.13 | 51 to 100 | EAF1 HO2 | Power Transformer
791 | SMP-1 | SMP-1 | 2x40.065 | 80.13 | 51 to 100 | EAF2 HO1 | Power Transformer
792 | SMP-1 | SMP-1 | 2x40.065 | 80.13 | 51 to 100 | EAF2 HO2 | Power Transformer
793 | SMP-1 | SMP-1 | 2x40.065 | 80.13 | 51 to 100 | EAF3 HO1 | Power Transformer
794 | SMP-1 | SMP-1 | 2x40.065 | 80.13 | 51 to 100 | EAF3-HO2 | Power Transformer
795 | SMP-1 | SMP-1 | 2x50.52 | 101.04 | 101 to 200 | EAF4 HO1 | Power Transformer
796 | SMP-1 | SMP-1 | 2x50.52 | 101.04 | 101 to 200 | EAF4 HO2 | Power Transformer
797 | SMP-1 | SMP-1 | 28 | 28 | 21 to 50 | LF1 | Power Transformer
798 | SMP-1 | SMP-1 | 28 | 28 | 21 to 50 | LF2 | Power Transformer
799 | SMP-1 | SMP-1 | 28 | 28 | 21 to 50 | LF3 | Power Transformer
800 | SMP-1 | SMP-1 | 30 | 30 | 21 to 50 | LF4 | Power Transformer
801 | SMP-1 | SMP-1 | 28 | 28 | 21 to 50 | LF5 | Power Transformer
802 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS1 CRANE TR1 | Power Transformer
803 | SMP-1 | SMP-1 | 2.5 | 2.5 | 3 to 5 | LCSS1 CRANE TR2 | Power Transformer
804 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-1 CASTER-1 | Power Transformer
807 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS1 EAF/LF T1 | Power Transformer
808 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS1 EAF/LF T2 | Power Transformer
809 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-1B TRAFO-1 | Power Transformer
810 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-1B TRAFO-2 | Power Transformer
811 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-1B TRAFO-3 | Power Transformer
812 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-5 TRAFO-1 | Power Transformer
813 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-5 TRAFO-2 | Power Transformer
814 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LCSS-5 TRAFO-3 | Power Transformer
815 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | FES 1&2 | Power Transformer
816 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | FE3 TRAF | Power Transformer
817 | SMP-1 | SMP-1 | 2.5 | 2.5 | 3 to 5 | DISTRI -FDC - NEW | Power Transformer
818 | SMP-1 | SMP-1 | 2.5 | 2.5 | 3 to 5 | FES-STEP6-TRAF2 | Power Transformer
819 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LIME TR-1 | Power Transformer
820 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LIME TR-2 | Power Transformer
821 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LIME TR-3 | Power Transformer
822 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | LIME TR-4 | Power Transformer
823 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | CASTER-2 TRAFO1 | Power Transformer
824 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | CASTER-2 TRAFO2 | Power Transformer
825 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | CASTER-3 TRAFO1 | Power Transformer
826 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | CASTER-3 TRAFO2 | Power Transformer
827 | SMP-1 | SMP-1 | 2X40.065 | 80.13 | 51 to 100 | EAF 1,2,3 SPARE (FAULTY) | Power Transformer
828 | SMP-1 | SMP-1 | 2X46.23 | 92.46 | 51 to 100 | EAF 1,2,3 SPARE | Power Transformer
829 | SMP-1 | SMP-1 | 2X50.00 | 100 | 51 to 100 | EAF -4-SPARE | Power Transformer
830 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | SPARE (Under Repair) | Power Transformer
831 | SMP-1 | SMP-1 | 2 | 2 | 1 to 2 | SPARE (Faulty) | Power Transformer
832 | SMP-1 | SMP-1 | 28 | 28 | 21 to 50 | LF -4 SPARE | Power Transformer
833 | SMP-1 | SMP-1 | 28 | 28 | 21 to 50 | LF -1,2,3,5 SPARE | Power Transformer
474 | SMP-2 | INI Caster T-2 | 2 | 2 | 1 to 2 | 07 OC 064/20 | Power Transformer | Normal | Normal | 11.08.2025 | 54 | 26 | 0.02 | 0.0009 | 1606 | Not detected | 37.9 | 178 | 0.827 | 4 | 2 | 2 | 3 | BDL | 75 | 3779 | 4 | 43752 | 31891 | Normal | Normal | 2025 | Aug
475 | SMP-2 | INI Caster T-3 | 2 | 2 | 1 to 2 | 07 OC 064/08 | Power Transformer | Normal | Normal | 11.08.2025 | 71 | 23 | 0.02 | 0.0005 | 1026 | Not detected | 39.4 | 172 | 0.827 | 5 | 2 | 2 | 3 | BDL | 47 | 1538 | 4 | 43062 | 31174 | Normal | Normal | 2025 | Aug
476 | SMP-2 | INI Caster T-4 | 2 | 2 | 1 to 2 | 07 OC 064/17 | Power Transformer | Normal | Normal | 11.08.2025 | 61 | 21 | 0.02 | 0.001 | 1682 | Not detected | 37.5 | 176 | 0.827 | 4 | 2 | 3 | 5 | BDL | 69 | 2170 | 5 | 44175 | 31899 | Normal | Normal | 2025 | Aug
477 | SMP-2 | CSP Caster 1&2 TR-1 | 2.5 | 2.5 | 3 to 5 | 08 PC 043/2 | Power Transformer | Normal | Normal | 11.08.2025 | 77 | 18 | 0.02 | 0.006 | 1555 | Not detected | 42.5 | 170 | 0.827 | 1 | 2 | 3 | 4 | BDL | 39 | 938 | 4 | 40678 | 21635 | Normal | Normal | 2025 | Aug
478 | SMP-2 | CSP Caster 1&2TR-2 | 2.5 | 2.5 | 3 to 5 | 08 PC 043/01 | Power Transformer | Normal | Normal | 11.08.2025 | 71 | 21 | 0.02 | 0.003 | 1751 | Not detected | 39.2 | 168 | 0.827 | 1 | 2 | 3 | 3 | BDL | 52 | 1531 | 4 | 40428 | 24732 | Normal | Normal | 2025 | Aug
479 | SMP-2 | CSP Caster 1&2 TR-3 | 2.5 | 2.5 | 3 to 5 | 08 PC 043/2 | Power Transformer | Normal | Normal | 11.08.2025 | 69 | 17 | 0.02 | 0.004 | 2005 | Not detected | 41.7 | 160 | 0.827 | 10 | 2 | 3 | 3 | BDL | 68 | 2401 | 5 | 43681 | 26665 | Normal | Normal | 2025 | Aug
480 | SMP-2 | CSP Caster 1&2 TR-4 | 2.5 | 2.5 | 3 to 5 | 08 PC 043/01 | Power Transformer | Normal | Normal | 11.08.2025 | 61 | 23 | 0.02 | 0.002 | 1883 | Not detected | 34.6 | 178 | 0.827 | 3 | 2 | 3 | 4 | BDL | 57 | 1886 | 5 | 42037 | 26028 | Normal | Normal | 2025 | Aug
481 | SMP-2 | CSP Caster 1&2 TR-5 | 2.5 | 2.5 | 3 to 5 | 08 PC 035/02 | Power Transformer | Normal | Normal | 11.08.2025 | 70 | 20 | 0.02 | 0.003 | 2514 | Not detected | 36.4 | 170 | 0.827 | 3 | 2 | 3 | 4 | BDL | 63 | 2089 | 4 | 44796 | 24450 | Normal | Normal | 2025 | Aug
482 | SMP-2 | CSP Caster 1&2 TR-6 | 2.5 | 2.5 | 3 to 5 | 08 PC 035/01 | Power Transformer | Normal | Normal | 11.08.2025 | 66 | 22 | 0.02 | 0.0005 | 137 | Not detected | 36.7 | 178 | 0.827 | 3 | 2 | 2 | 3 | BDL | 35 | 973 | 4 | 45709 | 26492 | Normal | Normal | 2025 | Aug
483 | SMP-2 | CSP Caster 3 TR-1 | 2.5 | 2.5 | 3 to 5 | 08 PC 035/04 | Power Transformer | Normal | Normal | 11.08.2025 | 70 | 22 | 0.02 | 0.0005 | 1976 | Not detected | 37.8 | 178 | 0.832 | 13 | 2 | 1 | 2 | BDL | 347 | 2922 | 4 | 37470 | 18881 | Normal | Normal | 2025 | Aug
484 | SMP-2 | CSP Caster 3 TR-2 | 2.5 | 2.5 | 3 to 5 | 08 PC 035/03 | Power Transformer | Normal | Normal | 11.08.2025 | 74 | 17 | 0.02 | 0.001 | 1314 | Not detected | 39.8 | 178 | 0.827 | 3 | 2 | 2 | 2 | BDL | 57 | 1595 | 4 | 43116 | 28173 | Normal | Normal | 2025 | Aug
485 | SMP-2 | CSP Caster 3 TR-3 | 2.5 | 2.5 | 3 to 5 | 08 PC 035/03 | Power Transformer | Normal | Normal | 11.08.2025 | 78 | 19 | 0.02 | 0.0003 | 2739 | Not detected | 42.9 | 176 | 0.827 | 1 | 1 | 2 | 1 | BDL | 38 | 1286 | 4 | 47022 | 25766 | Normal | Normal | 2025 | Aug
486 | SMP-2 | LBSS-1 TR-1 | 20/25 | 20 | 11 to 20 | 07 ZG010/01 | Power Transformer | Normal | Normal | 10.06.2025 | 57 | 29 | NA | NA | NA | NA | NA | NA | NA | 3 | 4 | 3 | 5 | BDL | 133 | 2937 | 5 | 41141 | 28347 | Normal | Normal | 2025 | Jun
487 | SMP-2 | LBSS-1 TR-2 | 20/25 | 20 | 11 to 20 | 07 ZG010/02 | Power Transformer | Normal | Normal | 10.06.2025 | 52 | 14 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 4 | BDL | 74 | 2216 | 5 | 39699 | 28611 | Normal | Normal | 2025 | Jun
488 | SMP-2 | LBSS-1 TR-3 | 2.5 | 2.5 | 3 to 5 | 08 PC036/01 | Power Transformer | Normal | Normal | 10.06.2025 | 55 | 17 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 40 | 773 | 5 | 39280 | 28518 | Normal | Normal | 2025 | Jun
489 | SMP-2 | LBSS-1 TR-4 | 2.5 | 2.5 | 3 to 5 | 08 PC036/02 | Power Transformer | Normal | Normal | 10.06.2025 | 62 | 14 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 2 | 2 | BDL | 31 | 608 | 4 | 32903 | 23824 | Normal | Normal | 2025 | Jun
490 | SMP-2 | LBSS-1 TR-5 | 2.5 | 2.5 | 3 to 5 | 08 PC036/05 | Power Transformer | Normal | Normal | 10.06.2025 | 52 | 21 | NA | NA | NA | NA | NA | NA | NA | 2 | 4 | 2 | 4 | BDL | 40 | 868 | 5 | 43552 | 31733 | Normal | Normal | 2025 | Jun
491 | SMP-2 | LBSS-1 TR-6 | 2.5 | 2.5 | 3 to 5 | 08 PC036/04 | Power Transformer | Normal | Normal | 11.06.2025 | 71 | 16 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 5 | BDL | 57 | 1041 | 5 | 40503 | 30112 | Normal | Normal | 2025 | Jun
492 | SMP-2 | LBSS-1 TR-7 | 2.5 | 2.5 | 3 to 5 | 08 PC036/03 | Power Transformer | Normal | Normal | 11.06.2025 | 52 | 21 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 1 | BDL | 36 | 689 | 5 | 41574 | 29561 | Normal | Normal | 2025 | Jun
493 | SMP-2 | LBSS-1 TR-8 | 3.15 | 3.15 | 3 to 5 | 08 CQC023/03 | Power Transformer | Normal | Normal | 11.06.2025 | 58 | 18 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 43 | 943 | 5 | 38736 | 28351 | Normal | Normal | 2025 | Jun
494 | SMP-2 | LBSS-1 TR-9 | 3.15 | 3.15 | 3 to 5 | 08 CQC023/02 | Power Transformer | Normal | Normal | 11.06.2025 | 66 | 21 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 2 | BDL | 44 | 1079 | 4 | 38666 | 28517 | Normal | Normal | 2025 | Jun
495 | SMP-2 | LBSS-1 TR-10 | 3.15 | 3.15 | 3 to 5 | 08 CQC023/01 | Power Transformer | Normal | Normal | 11.06.2025 | 56 | 20 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 1 | 1 | BDL | 40 | 763 | 5 | 41215 | 30063 | Normal | Normal | 2025 | Jun
496 | SMP-2 | LBSS-1 TR-11 | 1 | 1 | 1 to 2 | 08 LC078/01 | Power Transformer | Normal | Normal | 11.06.2025 | 67 | 18 | NA | NA | NA | NA | NA | NA | NA | 4 | 4 | 3 | 4 | BDL | 141 | 1280 | 5 | 42148 | 28105 | Normal | Normal | 2025 | Jun
497 | SMP-2 | LBSS-2 TR-1 | 20/25 | 20 | 11 to 20 | 07 ZG010/05 | Power Transformer | Normal | Normal | 11.06.2025 | 63 | 19 | NA | NA | NA | NA | NA | NA | NA | 2 | 4 | 3 | 4 | BDL | 78 | 2447 | 6 | 45227 | 31264 | Normal | Normal | 2025 | Jun
498 | SMP-2 | LBSS-2 TR-2 | 20/25 | 20 | 11 to 20 | 07 ZG010/07 | Power Transformer | Normal | Normal | 12.06.2025 | 60 | 15 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 10 | BDL | 66 | 1245 | 6 | 38906 | 28265 | Normal | Normal | 2025 | Jun
499 | SMP-2 | LBSS-2 TR-3 | 1 | 1 | 1 to 2 | 08 LC078/02 | Power Transformer | Normal | Normal | 12.06.2025 | 65 | 14 | NA | NA | NA | NA | NA | NA | NA | 5 | 3 | 3 | 3 | BDL | 37 | 740 | 6 | 40450 | 29453 | Normal | Normal | 2025 | Jun
500 | SMP-2 | LBSS-2 TR-4 | 2.5 | 2.5 | 3 to 5 | 08 PC036/07 | Power Transformer | Normal | Normal | 12.06.2025 | 64 | 29 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 33 | 464 | 5 | 39835 | 29115 | Normal | Normal | 2025 | Jun
501 | SMP-2 | LBSS-2 TR-5 | 2.5 | 2.5 | 3 to 5 | 08 PC036/06 | Power Transformer | Normal | Normal | 12.06.2025 | 64 | 22 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 5 | BDL | 43 | 1088 | 5 | 40618 | 29852 | Normal | Normal | 2025 | Jun
502 | SMP-2 | LBSS-2 TR-6 | 2.5 | 2.5 | 3 to 5 | 08 PC036/08 | Power Transformer | Normal | Normal | 13.06.2025 | 59 | 17 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 42 | 802 | 5 | 39343 | 29156 | Normal | Normal | 2025 | Jun
503 | SMP-2 | LBSS-2 TR-7 | 2.5 | 2.5 | 3 to 5 | 08 PC036/09 | Power Transformer | Normal | Normal | 13.06.2025 | 61 | 24 | NA | NA | NA | NA | NA | NA | NA | 1 | 4 | 3 | 4 | BDL | 49 | 1200 | 5 | 39751 | 30460 | Normal | Normal | 2025 | Jun
504 | SMP-2 | LBSS-2 TR-8 | 2.5 | 2.5 | 3 to 5 | 08 PC036/10 | Power Transformer | Normal | Normal | 13.06.2025 | 55 | 24 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 2 | BDL | 34 | 757 | 5 | 37957 | 28230 | Normal | Normal | 2025 | Jun
505 | SMP-2 | LBSS-2 TR-9 | 3.15 | 3.15 | 3 to 5 | 08 CQC023/04 | Power Transformer | Normal | Normal | 13.06.2025 | 65 | 24 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 46 | 1244 | 5 | 37983 | 27439 | Normal | Normal | 2025 | Jun
506 | SMP-2 | LBSS-2 TR-10 | 3.15 | 3.15 | 3 to 5 | 08 CQC023/05 | Power Transformer | Normal | Normal | 13.06.2025 | 71 | 28 | NA | NA | NA | NA | NA | NA | NA | 2 | 3 | 3 | 6 | BDL | 67 | 1872 | 5 | 41934 | 29623 | Normal | Normal | 2025 | Jun
507 | SMP-2 | Conarc-1 TR | 165 | 165 | 101 to 200 | 67653 | Power Transformer | Normal | Normal | 16.07.2025 | 70 | 10 | NA | NA | NA | NA | NA | NA | NA | 5 | 4 | 3 | 5 | BDL | 116 | 772 | 4 | 42363 | 23756 | Normal | Normal | 2025 | Jul
508 | SMP-2 | Conarc-1 Reactor | 165 | 165 | 101 to 200 | 67653 | Power Transformer | Normal | Normal | 16.07.2025 | 72 | 13 | NA | NA | NA | NA | NA | NA | NA | 5 | 3 | 3 | 7 | BDL | 150 | 1465 | 4 | 39812 | 21327 | Normal | Normal | 2025 | Jul
509 | SMP-2 | Conarc-2 TR | 165 | 165 | 101 to 200 | 66112 | Power Transformer | Normal | Normal | 16.07.2025 | 68 | 12 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 6 | BDL | 115 | 1003 | 4 | 42623 | 22568 | Normal | Normal | 2025 | Jul
510 | SMP-2 | Conarc-2 Reactor | 165 | 165 | 101 to 200 | 66112 | Power Transformer | Normal | Normal | 16.07.2025 | 75 | 9 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 125 | 1995 | 5 | 40447 | 22839 | Normal | Normal | 2025 | Jul
511 | SMP-2 | LHF-1 | 35 | 35 | 21 to 50 | 65960 | Power Transformer | Normal | Normal | 15.07.2025 | 74 | 15 | NA | NA | NA | NA | NA | NA | NA | 4 | 3 | 3 | 4 | 2 | 100 | 1283 | 4 | 40142 | 27957 | Normal | Normal | 2025 | Jul
512 | SMP-2 | LHF-2 | 35 | 35 | 21 to 50 | 65961 | Power Transformer | Normal | Normal | 15.07.2025 | 70 | 17 | NA | NA | NA | NA | NA | NA | NA | 7 | 3 | 2 | 2 | 2 | 60 | 916 | 3 | 39712 | 26857 | Normal | Normal | 2025 | Jul
513 | SMP-2 | LHF-3 | 35 | 35 | 21 to 50 | 66114 | Power Transformer | Normal | Normal | 15.07.2025 | 80 | 14 | NA | NA | NA | NA | NA | NA | NA | 7 | 7 | 3 | 19 | 3 | 73 | 1393 | 4 | 36286 | 22044 | Normal | Normal | 2025 | Jul
514 | SMP-2 | LHF-7 | 35 | 35 | 21 to 50 | 66114 | Power Transformer | Normal | Normal | 15.07.2025 | 71 | 19 | NA | NA | NA | NA | NA | NA | NA | 7 | 3 | 3 | 5 | BDL | 74 | 1279 | 5 | 44633 | 24912 | Normal | Normal | 2025 | Jul
515 | SMP-2 | KILN-5 | 2.5 | 2.5 | 3 to 5 | 08PC-041/02 | Power Transformer | Normal | Normal | 13.06.2025 | 56 | 21 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 39 | 816 | 5 | 42118 | 30656 | Normal | Normal | 2025 | Jun
516 | SMP-2 | KILN-6 | 2 | 2 | 1 to 2 | 070C-064 | Power Transformer | Normal | Normal | 13.06.2025 | 56 | 20 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 3 | BDL | 42 | 894 | 5 | 40106 | 28746 | Normal | Normal | 2025 | Jun
517 | SMP-2 | KILN-7 | 2 | 2 | 1 to 2 | 070C-064/13 | Power Transformer | Normal | Normal | 13.06.2025 | 47 | 29 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 5 | BDL | 35 | 904 | 5 | 40383 | 29561 | Normal | Normal | 2025 | Jun
518 | SMP-2 | KILN-8 | 2.5 | 2.5 | 3 to 5 | PC 057/01 | Power Transformer | Normal | Normal | 13.06.2025 | 68 | 22 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 8 | BDL | 28 | 767 | 8 | 35379 | 22128 | Normal | Normal | 2025 | Jun
834 | SMP-2 | LCSS-5, INI Caster | 2 | 2 | 1 to 2 | T-2 | Power Transformer
835 | SMP-2 | LCSS-5, INI Caster | 2 | 2 | 1 to 2 | T-3 | Power Transformer
836 | SMP-2 | LCSS-5, INI Caster | 2 | 2 | 1 to 2 | T-4 | Power Transformer
837 | SMP-2 | CSP Caster 1&2- ECR | 2.5 | 2.5 | 3 to 5 | TR-1 | Power Transformer
838 | SMP-2 | CSP Caster 1&2- ECR | 2.5 | 2.5 | 3 to 5 | TR-2 | Power Transformer
839 | SMP-2 | CSP Caster 1&2- ECR | 2.5 | 2.5 | 3 to 5 | TR-3 | Power Transformer
840 | SMP-2 | CSP Caster 1&2- ECR | 2.5 | 2.5 | 3 to 5 | TR-4 | Power Transformer
841 | SMP-2 | CSP Caster 1&2- ECR | 2.5 | 2.5 | 3 to 5 | TR-5 | Power Transformer
842 | SMP-2 | CSP Caster 1&2- ECR | 2.5 | 2.5 | 3 to 5 | TR-6 | Power Transformer
843 | SMP-2 | CSP Caster 3- ECR | 2.5 | 2.5 | 3 to 5 | TR-1 | Power Transformer
844 | SMP-2 | CSP Caster 3- ECR | 2.5 | 2.5 | 3 to 5 | TR-2 | Power Transformer
845 | SMP-2 | CSP Caster 3- ECR | 2.5 | 2.5 | 3 to 5 | TR-3 | Power Transformer
846 | SMP-2 | LBSS-1 | 20/25 | 20 | 11 to 20 | TR-1 | Power Transformer
847 | SMP-2 | LBSS-1 | 20/25 | 20 | 11 to 20 | TR-2 | Power Transformer
848 | SMP-2 | LBSS-1 | 2.5 | 2.5 | 3 to 5 | TR-3 | Power Transformer
849 | SMP-2 | LBSS-1 | 2.5 | 2.5 | 3 to 5 | TR-4 | Power Transformer
850 | SMP-2 | LBSS-1 | 2.5 | 2.5 | 3 to 5 | TR-5 | Power Transformer
851 | SMP-2 | LBSS-1 | 2.5 | 2.5 | 3 to 5 | TR-6 | Power Transformer
852 | SMP-2 | LBSS-1 | 2.5 | 2.5 | 3 to 5 | TR-7 | Power Transformer
853 | SMP-2 | LBSS-1 | 3.15 | 3.15 | 3 to 5 | TR-8 | Power Transformer
854 | SMP-2 | LBSS-1 | 3.15 | 3.15 | 3 to 5 | TR-9 | Power Transformer
855 | SMP-2 | LBSS-1 | 3.15 | 3.15 | 3 to 5 | TR-10 | Power Transformer
856 | SMP-2 | LBSS-1 | 1 | 1 | 1 to 2 | TR-11 | Power Transformer
857 | SMP-2 | LBSS-2 | 20/25 | 20 | 11 to 20 | TR-1 | Power Transformer
858 | SMP-2 | LBSS-2 | 20/25 | 20 | 11 to 20 | TR-2 | Power Transformer
859 | SMP-2 | LBSS-2 | 1 | 1 | 1 to 2 | TR-3 | Power Transformer
860 | SMP-2 | LBSS-2 | 2.5 | 2.5 | 3 to 5 | TR-4 | Power Transformer
861 | SMP-2 | LBSS-2 | 2.5 | 2.5 | 3 to 5 | TR-5 | Power Transformer
862 | SMP-2 | LBSS-2 | 2.5 | 2.5 | 3 to 5 | TR-6 | Power Transformer
863 | SMP-2 | LBSS-2 | 2.5 | 2.5 | 3 to 5 | TR-7 | Power Transformer
864 | SMP-2 | LBSS-2 | 2.5 | 2.5 | 3 to 5 | TR-8 | Power Transformer
865 | SMP-2 | LBSS-2 | 3.15 | 3.15 | 3 to 5 | TR-9 | Power Transformer
866 | SMP-2 | LBSS-2 | 3.15 | 3.15 | 3 to 5 | TR-10 | Power Transformer
867 | SMP-2 | CONARC-1 | 165 | 165 | 101 to 200 | Conarc-Transformer | Power Transformer
868 | SMP-2 | CONARC-2 | 165 | 165 | 101 to 200 | Conarc-Transformer | Power Transformer
869 | SMP-2 | LHF-1 | 35 | 35 | 21 to 50 | LHF-1 Transformer(On line) | Power Transformer
870 | SMP-2 | LHF-2 | 35 | 35 | 21 to 50 | LHF-2 Transformer(Off line) | Power Transformer
871 | SMP-2 | LHF-3 | 35 | 35 | 21 to 50 | LHF-3 Transformer(On line) | Power Transformer
872 | SMP-2 | LHF-7 | 35 | 35 | 21 to 50 | LHF-7 Transformer(Off Line) | Power Transformer
873 | SMP-2 | LIMEPLANT-B ECR-2 | 2.5 | 2.5 | 3 to 5 | KILN-5 | Power Transformer
874 | SMP-2 | LIMEPLANT-B ECR-2 | 2 | 2 | 1 to 2 | KILN-6 | Power Transformer
875 | SMP-2 | LIMEPLANT-B ECR-2 | 2 | 2 | 1 to 2 | KILN-7 | Power Transformer
876 | SMP-2 | LIMEPLANT-B ECR-2 | 2.5 | 2.5 | 3 to 5 | KILN-8 | Power Transformer
877 | SMP-2 | FES | 4 | 4 | 3 to 5 | FES-2 Id Fan Standby MV Drive TR | Power Transformer
878 | SMP-2 | CONARC TRANSFORMER | 165 | 165 | 101 to 200 | SPARE | Power Transformer
519 | Transmission | 500 MVA ICT #1 | 500 | 500 | Above 200 | B-30579 | Power Transformer | Normal | Normal | 15.07.2025 | 86 | 9 | NA | NA | NA | NA | NA | NA | NA | 27 | 14 | 3 | 6 | BDL | 333 | 2304 | 3 | 22256 | 8173 | Normal | Normal | 2025 | Jul
520 | Transmission | 500 MVA ICT #2 | 500 | 500 | Above 200 | B-30580 | Power Transformer | Moderate |  | 04.09.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 41 | 70 | 8 | 91 | 2 | 205 | 1245 | 12 | 14708 | 9625 | Moderate |  | 2025 | Sep
521 | Transmission | 500 MVA ICT #3 | 500 | 500 | Above 200 | 14113-001 | Power Transformer | Normal |  | 17.09.2025 |  | NA | NA | NA | NA | NA | NA | NA | NA | 4 | 1 | 1 | 1 | BDL | 91 | 412 | 2 | 22315 | 10728 | Normal |  | 2025 | Sep
522 | Transmission | 1 MVA Aux Trafo #1 | 1 | 1 | 1 to 2 | 82930 | Power Transformer | Normal | Normal | 15.07.2025 | 73 | 14 | NA | NA | NA | NA | NA | NA | NA | 11 | 2 | 1 | 5 | BDL | 123 | 1491 | 5 | 33765 | 14912 | Normal | Normal | 2025 | Jul
523 | Transmission | 1 MVA Aux Trafo #2 | 1 | 1 | 1 to 2 | 82931 | Power Transformer | Normal | Normal | 15.07.2025 | 56 | 20 | NA | NA | NA | NA | NA | NA | NA | 8 | 2 | 1 | 3 | BDL | 101 | 1170 | 5 | 43058 | 16198 | Normal | Normal | 2025 | Jul
636 | Transmission | Power Transmission | 500 | 500 | Above 200 | 500 MVA ICT #1 | Power Transformer
637 | Transmission | Power Transmission | 500 | 500 | Above 200 | 500 MVA ICT #2 | Power Transformer
638 | Transmission | Power Transmission | 500 | 500 | Above 200 | 500 MVA ICT #3 | Power Transformer
639 | Transmission | Power Transmission | 1 | 1 | 1 to 2 | 1 MVA Aux Trafo #1 | Power Transformer
640 | Transmission | Power Transmission | 1 | 1 | 1 to 2 | 1 MVA Aux Trafo #2 | Power Transformer
524 | UTILITY | EAF 1/2 PH TR-1 | 2 | 2 | 1 to 2 | 3055/16 | Power Transformer | Normal | Normal | 15.05.2025 | 56 | 19 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 7 | BDL | 132 | 3506 | 6 | 35247 | 16845 | Normal | Normal | 2025 | May
525 | UTILITY | EAF 1/2 PH TR-2 | 2 | 2 | 1 to 2 | 3055/11 | Power Transformer | Normal | Normal | 15.05.2025 | 54 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 4 | 5 | BDL | 103 | 3150 | 7 | 36458 | 16755 | Normal | Normal | 2025 | May
526 | UTILITY | NRWPH TR-1 | 2 | 2 | 1 to 2 | 07-0C-064/22 | Power Transformer | Normal | Normal | 15.05.2025 | 62 | 18 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 5 | BDL | 34 | 1070 | 5 | 39259 | 18863 | Normal | Normal | 2025 | May
527 | UTILITY | NRWPH TR-2 | 2 | 2 | 1 to 2 | 07-0C-064/21 | Power Transformer | Normal | Normal | 15.05.2025 | 65 | 15 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 6 | BDL | 43 | 1330 | 5 | 39456 | 19651 | Normal | Normal | 2025 | May
528 | UTILITY | CHILLER TR | 2 | 2 | 1 to 2 | 12078/1 | Power Transformer | Normal | Normal | 15.05.2025 | 44 | 33 | NA | NA | NA | NA | NA | NA | NA | 2 | 2 | 3 | 4 | BDL | 40 | 729 | 5 | 38753 | 18359 | Normal | Normal | 2025 | May
529 | UTILITY | CR-1 | 2 | 2 | 1 to 2 | 11711/1 | Power Transformer | Normal | Normal | 15.05.2025 | 53 | 25 | NA | NA | NA | NA | NA | NA | NA | 1 | 2 | 3 | 4 | BDL | 27 | 735 | 5 | 37752 | 17470 | Normal | Normal | 2025 | May
530 | UTILITY | EAF 3 PH TR-1 | 2 | 2 | 1 to 2 | 3291/5 | Power Transformer | Normal | Moderate | 16.05.2025 | 42 | 44 | NA | NA | NA | NA | NA | NA | NA | 6 | 2 | 3 | 3 | BDL | 114 | 4091 | 8 | 25753 | 12227 | Normal | Moderate | 2025 | May
531 | UTILITY | EAF 3 PH TR-2 | 2 | 2 | 1 to 2 | 3291/6 | Power Transformer | Normal | Moderate | 16.05.2025 | 49 | 58 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 4 | 6 | BDL | 170 | 4832 | 11 | 30712 | 14695 | Normal | Moderate | 2025 | May
532 | UTILITY | HSM PH TR-1 | 2 | 2 | 1 to 2 | 3055/12 | Power Transformer | Normal | Normal | 16.05.2025 | 49 | 34 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 4 | 22 | BDL | 85 | 1963 | 8 | 28356 | 14129 | Normal | Normal | 2025 | May
533 | UTILITY | HSM PH TR-2 | 2 | 2 | 1 to 2 | 13810/1 | Power Transformer | Normal | Moderate | 16.05.2025 | 46 | 50 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 4 | 3 | BDL | 150 | 6067 | 8 | 28863 | 13529 | Normal | Moderate | 2025 | May
534 | UTILITY | LCSS-2 TR-1 | 2 | 2 | 1 to 2 | 3055/6 | Power Transformer | Normal | Normal | 16.05.2025 | 42 | 40 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 3 | 3 | BDL | 65 | 2112 | 5 | 27812 | 13218 | Normal | Normal | 2025 | May
535 | UTILITY | LCSS-2 TR-2 | 2 | 2 | 1 to 2 | 3055/5 | Power Transformer | Normal | Normal | 16.05.2025 | 54 | 37 | NA | NA | NA | NA | NA | NA | NA | 5 | 2 | 3 | 3 | BDL | 77 | 2471 | 5 | 28819 | 13096 | Normal | Normal | 2025 | May
536 | UTILITY | LBSS-2 TR-1 | 20 | 20 | 11 to 20 | 2800054084 | Power Transformer | Normal | Normal | 17.05.2025 | 63 | 13 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 3 | BDL | 81 | 1175 | 5 | 33764 | 13833 | Normal | Normal | 2025 | May
537 | UTILITY | LBSS-2 TR-2 | 20 | 20 | 11 to 20 | 2800054083 | Power Transformer | Normal | Normal | 17.05.2025 | 64 | 20 | NA | NA | NA | NA | NA | NA | NA | 4 | 2 | 2 | 2 | BDL | 73 | 1164 | 5 | 32165 | 14046 | Normal | Normal | 2025 | May
538 | UTILITY | LBSS-2 TR-3 | 20 | 20 | 11 to 20 | J885 | Power Transformer | Normal | Normal | 17.05.2025 | 66 | 10 | NA | NA | NA | NA | NA | NA | NA | 3 | 2 | 2 | 3 | BDL | 65 | 767 | 5 | 35044 | 16047 | Normal | Normal | 2025 | May
539 | UTILITY | VARIAV-OLD AMNS | 2.5 | 2.5 | 3 to 5 | 4110/1 | Power Transformer | Normal | Normal | 08.06.2025 | 69 | 26 | NA | NA | NA | NA | NA | NA | NA | 1 | 3 | 3 | 4 | BDL | 63 | 707 | 5 | 38691 | 27052 | Normal | Normal | 2025 | Jun
540 | UTILITY | VARIAV-OLD RAMA | 2.5 | 2.5 | 3 to 5 | 4110/2 | Power Transformer | Normal | Normal | 08.06.2025 | 77 | 21 | NA | NA | NA | NA | NA | NA | NA | 3 | 3 | 3 | 4 | BDL | 59 | 1011 | 5 | 39182 | 27810 | Normal | Normal | 2025 | Jun
541 | UTILITY | VARIAV-NEW RAMA | 1 | 1 | 1 to 2 | 08LD-356/02 | Power Transformer | Normal | Normal | 08.06.2025 | 52 | 22 | NA | NA | NA | NA | NA | NA | NA | 11 | 5 | 3 | 6 | BDL | 282 | 1699 | 6 | 38156 | 22794 | Normal | Normal | 2025 | Jun
542 | UTILITY | VARIAV-NEW AMNS | 1 | 1 | 1 to 2 | 08LD-356/01 | Power Transformer | Normal | Normal | 08.06.2025 | 75 | 20 | NA | NA | NA | NA | NA | NA | NA | 9 | 4 | 3 | 6 | BDL | 198 | 1489 | 5 | 41779 | 26186 | Normal | Normal | 2025 | Jun
543 | UTILITY | VARIAV-OLD LIGHTING | 0.1 | 0.1 | 0 - 0.9 | 15/271 | Distribution Transformer | Normal | Normal | 22.02.2025 | 70 | 22 | 0.03 | 0.11 | 2 | Not detected | 21.1 | 168 | 0.852 | 1 | 2 | 3 | 3 | BDL | 31 | 1012 | 5 | 39653 | 27639 | Normal | Normal | 2025 | Feb
544 | UTILITY | LCSS-3 TR-1 | 2 | 2 | 1 to 2 | 3084/1 | Power Transformer | Normal | Normal | 18.12.2024 | 67 | 15 | 0.02 | 0.009 | 778 | Not detected | 38.9 | 172 | 0.822 | 2 | 2 | 3 | 3 | BDL | 43 | 1675 | 5 | 38295 | 27338 | Normal | Normal | 2024 | Dec
545 | UTILITY | BF RWTP | 0.63 | 0.63 | 0 - 0.9 | 09JC-029/01 | Distribution Transformer | Normal | Normal | 22.06.2024 | 74 | 20 | NA | NA | NA | NA | NA | NA | NA | 6 | 1 | 1 | 4 | BDL | 68 | 1104 | 6 | 50707 | 31744 | Normal | Normal | 2024 | Jun
546 | UTILITY | LBSS-4 Trafo-1 | 20/25 | 20 | 11 to 20 | 07-ZG 010-07 | Power Transformer | Normal | Normal | 17.03.2025 | 70 | 8 | 0.02 | 0.001 | 678 | Not detected | 43.8 | 176 | 0.832 | 6 | 3 | 2 | 3 | BDL | 226 | 1320 | 4 | 41256 | 21370 | Normal | Normal | 2025 | Mar
547 | UTILITY | LBSS-4 Trafo-2 | 20/25 | 20 | 11 to 20 | 07-ZG 010-08 | Power Transformer | Normal | Normal | 17.03.2025 | 77 | 19 | 0.02 | 0.005 | 459 | Not detected | 35.3 | 154 | 0.827 | 2 | 4 | 3 | 4 | BDL | 68 | 1734 | 5 | 49856 | 29068 | Normal | Normal | 2025 | Mar
548 | UTILITY | LBSS-4 Trafo-3 | 20/25 | 20 | 11 to 20 | 07-ZG 010-09 | Power Transformer | Normal | Normal | 17.03.2025 | 66 | 17 | 0.02 | 0.004 | 207 | Not detected | 34.1 | 154 | 0.827 | 1 | 3 | 4 | 14 | BDL | 72 | 2094 | 5 | 46528 | 28712 | Normal | Normal | 2025 | Mar
549 | UTILITY | LBSS-3 Trafo-1 | 12.5/16.5 | 12.5 | 11 to 20 | TP-95-8025 | Power Transformer | Normal | Normal | 12.03.2025 | 69 | 11 | 0.02 | 0.004 | 1826 | Not detected | 40.3 | 158 | 0.827 | 2 | 4 | 3 | 3 | BDL | 50 | 2308 | 5 | 42211 | 32707 | Normal | Normal | 2025 | Mar
550 | UTILITY | LBSS-3 Trafo-2 | 12.5/16.5 | 12.5 | 11 to 20 | TP-95-8024 | Power Transformer | Normal | Normal | 12.03.2025 | 70 | 16 | 0.02 | 0.004 | 1782 | Not detected | 40.7 | 166 | 0.827 | 2 | 4 | 3 | 4 | BDL | 106 | 4292 | 5 | 49557 | 29745 | Normal | Normal | 2025 | Mar
551 | UTILITY | LBSS-4 Trafor-1 for PMCC-11 | 2.5 | 2.5 | 3 to 5 | 07-PC024/22 | Power Transformer | Normal | Normal | 13.03.2025 | 67 | 24 | 0.02 | 0.0004 | 3608 | Not detected | 38 | 160 | 0.827 | 2 | 3 | 3 | 3 | BDL | 31 | 636 | 5 | 42564 | 32243 | Normal | Normal | 2025 | Mar
552 | UTILITY | LBSS-4 Trafor-2 for PMCC-11 | 2.5 | 2.5 | 3 to 5 | 07-PC024/23 | Power Transformer | Normal | Normal | 13.03.2025 | 69 | 20 | 0.02 | 0.009 | 1417 | Not detected | 39.5 | 158 | 0.827 | 2 | 4 | 3 | 5 | BDL | 41 | 1542 | 5 | 49557 | 31199 | Normal | Normal | 2025 | Mar
553 | UTILITY | LBSS-4 Trafor-1 for PMCC-09 | 2.5 | 2.5 | 3 to 5 | 07-PC024/24 | Power Transformer | Normal | Normal | 12.03.2025 | 74 | 15 | 0.02 | 0.008 | 2574 | Not detected | 37.9 | 160 | 0.827 | 1 | 3 | 3 | 6 | BDL | 35 | 1278 | 5 | 47671 | 31028 | Normal | Normal | 2025 | Mar
554 | UTILITY | LBSS-4 Trafor-2 for PMCC-09 | 2.5 | 2.5 | 3 to 5 | 07-PC024/31 | Power Transformer | Normal | Normal | 12.03.2025 | 66 | 23 | 0.02 | 0.001 | 1809 | Not detected | 37.4 | 164 | 0.827 | 2 | 3 | 3 | 5 | BDL | 38 | 1416 | 4 | 49781 | 31100 | Normal | Normal | 2025 | Mar
555 | UTILITY | LBSS-4 Trafor-3 for PMCC-09 | 2.5 | 2.5 | 3 to 5 | 07-PC024/28 | Power Transformer | Normal | Normal | 12.03.2025 | 51 | 21 | 0.02 | 0.001 | 3275 | Not detected | 38.6 | 164 | 0.827 | 1 | 4 | 3 | 3 | BDL | 31 | 863 | 5 | 49256 | 30886 | Normal | Normal | 2025 | Mar
556 | UTILITY | LBSS-4 Trafo -1 for PMCC-10 | 2.5 | 2.5 | 3 to 5 | 07-PC024/20 | Power Transformer | Normal | Normal | 17.03.2025 | 66 | 23 | 0.02 | 0.001 | 1875 | Not detected | 42.1 | 160 | 0.832 | 1 | 2 | 3 | 4 | BDL | 43 | 807 | 5 | 45236 | 29423 | Normal | Normal | 2025 | Mar
557 | UTILITY | LBSS-4 Trafo -2 for PMCC-10 | 2.5 | 2.5 | 3 to 5 | 07-PC024/29 | Power Transformer | Normal | Normal | 17.03.2025 | 59 | 24 | 0.02 | 0.0003 | 1519 | Not detected | 35 | 162 | 0.832 | 1 | 2 | 3 | 9 | BDL | 51 | 1369 | 7 | 50145 | 27895 | Normal | Normal | 2025 | Mar
558 | UTILITY | LBSS-4 Trafo -3 for PMCC-10 | 2.5 | 2.5 | 3 to 5 | 07-PC024/30 | Power Transformer | Normal | Normal | 13.03.2025 | 63 | 23 | 0.02 | 0.0004 | 3051 | Not detected | 37.9 | 164 | 0.827 | 1 | 3 | 3 | 5 | BDL | 37 | 1405 | 5 | 46258 | 24356 | Normal | Normal | 2025 | Mar
559 | UTILITY | LBSS-4 Trafo -1 for MLDB | 2 | 2 | 1 to 2 | 07 OC 064/6 | Power Transformer | Normal | Normal | 12.03.2025 | 70 | 24 | 0.02 | 0.001 | 1968 | Not detected | 39.7 | 172 | 0.832 | 1 | 4 | 4 | 6 | 2 | 25 | 901 | 5 | 47650 | 31019 | Normal | Normal | 2025 | Mar
560 | UTILITY | LBSS-4 Trafo -2 for MLDB | 2 | 2 | 1 to 2 | 07 OC 064/5 | Power Transformer | Normal | Normal | 12.03.2025 | 60 | 18 | 0.02 | 0.005 | 2861 | Not detected | 41.4 | 162 | 0.827 | 1 | 2 | 3 | 4 | BDL | 22 | 989 | 4 | 43602 | 31419 | Normal | Normal | 2025 | Mar
561 | UTILITY | HMPS Trafo-1 for PMCC-14 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/21 | Power Transformer | Normal | Normal | 17.03.2025 | 70 | 20 | 0.02 | 0.001 | 1434 | Not detected | 41.1 | 156 | 0.832 | 1 | 2 | 3 | 4 | BDL | 43 | 583 | 5 | 48524 | 24077 | Normal | Normal | 2025 | Mar
562 | UTILITY | HMPS Trafo-2 for PMCC-14 | 2.5 | 2.5 | 3 to 5 | 07 PC 024/19 | Power Transformer | Normal | Normal | 17.03.2025 | 70 | 13 | 0.02 | 0.004 | 815 | Not detected | 40.9 | 158 | 0.832 | 1 | 2 | 4 | 14 | BDL | 54 | 1854 | 5 | 47856 | 31970 | Normal | Normal | 2025 | Mar
563 | UTILITY | Trafor-1 for PMCC-08 | 2.5 | 2.5 | 3 to 5 | 09 PC 044/05 | Power Transformer | Normal | Normal | 17.03.2025 | 60 | 22 | 0.02 | 0.001 | 2243 | Not detected | 34 | 162 | 0.832 | 5 | 3 | 3 | 5 | BDL | 35 | 1522 | 5 | 48526 | 29944 | Normal | Normal | 2025 | Mar
564 | UTILITY | Trafor-2 for PMCC-08 | 2.5 | 2.5 | 3 to 5 | 09 PC 044/06 | Power Transformer | Normal | Normal | 17.03.2025 | 64 | 23 | 0.02 | 0.002 | 956 | Not detected | 35.4 | 172 | 0.832 | 1 | 2 | 3 | 3 | BDL | 44 | 1130 | 5 | 56248 | 27122 | Normal | Normal | 2025 | Mar
565 | UTILITY | Trafor-1 for PMCC-05 | 2.5 | 2.5 | 3 to 5 | 09 PC 044/01 | Power Transformer | Normal | Normal | 15.03.2025 | 69 | 18 | 0.02 | 0.001 | 3645 | Not detected | 41 | 158 | 0.827 | 1 | 3 | 3 | 5 | BDL | 20 | 937 | 5 | 49852 | 30036 | Normal | Normal | 2025 | Mar
566 | UTILITY | Trafor-2 for PMCC-05 | 2.5 | 2.5 | 3 to 5 | 09 PC 044/02 | Power Transformer | Normal | Normal | 15.03.2025 | 69 | 25 | 0.02 | 0.005 | 1318 | Not detected | 42.4 | 164 | 0.827 | 1 | 3 | 3 | 3 | BDL | 28 | 736 | 5 | 49232 | 31098 | Normal | Normal | 2025 | Mar
567 | UTILITY | Trafor-1 for PMCC-06 | 2.5 | 2.5 | 3 to 5 | 07-PC-024/27 | Power Transformer | Normal | Normal | 13.03.2025 | 75 | 15 | 0.02 | 0.0003 | 3458 | Not detected | 39.8 | 160 | 0.827 | 1 | 3 | 3 | 6 | BDL | 32 | 1418 | 5 | 45222 | 31396 | Normal | Normal | 2025 | Mar
568 | UTILITY | Trafor-2 for PMCC-06 | 2.5 | 2.5 | 3 to 5 | 07-PC-024/25 | Power Transformer | Normal | Normal | 13.03.2025 | 51 | 21 | 0.02 | 0.001 | 1932 | Not detected | 38.2 | 164 | 0.827 | 1 | 3 | 3 | 5 | BDL | 38 | 1230 | 5 | 51201 | 30800 | Normal | Normal | 2025 | Mar
569 | UTILITY | Trafor-1 for PMCC-07 | 2.5 | 2.5 | 3 to 5 | 07-PC-024/32 | Power Transformer | Normal | Normal | 13.03.2025 | 66 | 19 | 0.02 | 0.001 | 4309 | Not detected | 40.7 | 158 | 0.827 | 2 | 3 | 3 | 3 | BDL | 25 | 617 | 6 | 42225 | 21826 | Normal | Normal | 2025 | Mar
570 | UTILITY | Trafor-2 for PMCC-07 | 2.5 | 2.5 | 3 to 5 | 07-PC-024/26 | Power Transformer | Normal | Normal | 13.03.2025 | 69 | 18 | 0.02 | 0.001 | 2510 | Not detected | 39.8 | 164 | 0.827 | 1 | 3 | 3 | 3 | BDL | 33 | 1513 | 5 | 49557 | 29881 | Normal | Normal | 2025 | Mar
571 | UTILITY | Trafor-1 for MLDB | 2 | 2 | 1 to 2 | 07-OC-064/7 | Power Transformer | Normal | Normal | 12.03.2025 | 77 | 21 | 0.02 | 0.003 | 1912 | Not detected | 39.5 | 166 | 0.832 | 1 | 3 | 3 | 4 | BDL | 23 | 819 | 4 | 48730 | 27781 | Normal | Normal | 2025 | Mar
572 | UTILITY | Trafor-1 for PMCC-15 | 2.5 | 2.5 | 3 to 5 | 09- PC-044/03 | Power Transformer | Normal | Normal | 15.03.2025 | 67 | 13 | 0.02 | 0.001 | 3421 | Not detected | 35.5 | 166 | 0.827 | 1 | 3 | 3 | 4 | BDL | 36 | 979 | 5 | 48652 | 28522 | Normal | Normal | 2025 | Mar
573 | UTILITY | Trafor-2 for PMCC-15 | 2.5 | 2.5 | 3 to 5 | 09-PC-044/04 | Power Transformer | Normal | Normal | 15.03.2025 | 49 | 26 | 0.02 | 0.003 | 109 | Not detected | 31.6 | 166 | 0.827 | 1 | 4 | 3 | 3 | BDL | 36 | 930 | 5 | 47254 | 30018 | Normal | Normal | 2025 | Mar
574 | UTILITY | Trafor for MOD-5 FWPH MCC | 2 | 2 | 1 to 2 | 05 OC-048/03 | Power Transformer | Normal | Normal | 15.03.2025 | 65 | 18 | 0.02 | 0.01 | 41 | Not detected | 29.8 | 164 | 0.827 | 11 | 4 | 3 | 7 | BDL | 214 | 1746 | 5 | 48625 | 24356 | Normal | Normal | 2025 | Mar
1014 | UTILITY | LBSS-4 | 20/25 | 20 | 11 to 20 | Trafo-1 | Power Transformer
1015 | UTILITY | LBSS-4 | 20/25 | 20 | 11 to 20 | Trafo-2 | Power Transformer
1016 | UTILITY | LBSS-4 | 20/25 | 20 | 11 to 20 | Trafo-3 | Power Transformer
1017 | UTILITY | LBSS-3 | 12.5/16.5 | 12.5 | 11 to 20 | Trafo-1 | Power Transformer
1018 | UTILITY | LBSS-3 | 12.5/16.5 | 12.5 | 11 to 20 | Trafo-2 | Power Transformer
1019 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-11 | Power Transformer
1020 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-11 | Power Transformer
1021 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-09 | Power Transformer
1022 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-09 | Power Transformer
1023 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-3 for PMCC-09 | Power Transformer
1024 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-10 | Power Transformer
1025 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-10 | Power Transformer
1026 | UTILITY | LBSS-4 | 2.5 | 2.5 | 3 to 5 | Trafor-3 for PMCC-10 | Power Transformer
1027 | UTILITY | LBSS-4 | 2 | 2 | 1 to 2 | Trafor-1 for MLDB | Power Transformer
1028 | UTILITY | LBSS-4 | 2 | 2 | 1 to 2 | Trafor-2 for MLDB | Power Transformer
1029 | UTILITY | HMPS | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-14 | Power Transformer
1030 | UTILITY | HMPS | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-14 | Power Transformer
1031 | UTILITY | C.H-1 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-08 | Power Transformer
1032 | UTILITY | C.H-1 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-08 | Power Transformer
1033 | UTILITY | C.H-2 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-05 | Power Transformer
1034 | UTILITY | C.H-2 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-05 | Power Transformer
1035 | UTILITY | LBSS-3 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-06 | Power Transformer
1036 | UTILITY | LBSS-3 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-06 | Power Transformer
1037 | UTILITY | LBSS-3 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-07 | Power Transformer
1038 | UTILITY | LBSS-3 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-07 | Power Transformer
1039 | UTILITY | LBSS-3 | 2 | 2 | 1 to 2 | Trafor-1 for MLDB | Power Transformer
1040 | UTILITY | FINFAN-2 | 2.5 | 2.5 | 3 to 5 | Trafor-1 for PMCC-15 | Power Transformer
1041 | UTILITY | FINFAN-2 | 2.5 | 2.5 | 3 to 5 | Trafor-2 for PMCC-15 | Power Transformer
1042 | UTILITY | MOD-5 FWPH | 2 | 2 | 1 to 2 | Trafor for MOD-5 FWPH MCC | Power Transformer
1043 | UTILITY | LBSS-2 | 20 | 20 | 11 to 20 | Trafo-1 | Power Transformer
1044 | UTILITY | LBSS-2 | 20 | 20 | 11 to 20 | Trafo-2 | Power Transformer
1045 | UTILITY | LBSS-2 | 20 | 20 | 11 to 20 | Traffo-3 | Power Transformer
1046 | UTILITY | LCSS-2 | 2 | 2 | 1 to 2 | Trafo-1 | Power Transformer
1047 | UTILITY | LCSS-2 | 2 | 2 | 1 to 2 | Trafo-2 | Power Transformer
1048 | UTILITY | EAF 1/2 PH | 2 | 2 | 1 to 2 | Trafo-1 | Power Transformer
1049 | UTILITY | EAF 1/2 PH | 2 | 2 | 1 to 2 | Trafo-2 | Power Transformer
1050 | UTILITY | HSM PH | 2 | 2 | 1 to 2 | Trafo-1 | Power Transformer
1051 | UTILITY | HSM PH | 2 | 2 | 1 to 2 | Trafo-2 | Power Transformer
1052 | UTILITY | CHILLER | 2 | 2 | 1 to 2 | Trafo | Power Transformer
1053 | UTILITY | CR-1 | 2 | 2 | 1 to 2 | Trafo | Power Transformer
1054 | UTILITY | LCSS-3 | 0.5 | 0.5 | 0 - 0.9 | Trafo-2 | Distribution Transformer
1055 | UTILITY | EAF 3 PH | 2 | 2 | 1 to 2 | Trafo-1 | Power Transformer
1056 | UTILITY | EAF 3 PH | 2 | 2 | 1 to 2 | Trafo-2 | Power Transformer
1057 | UTILITY | NRWPH | 2 | 2 | 1 to 2 | Trafo-1 | Power Transformer
1058 | UTILITY | NRWPH | 2 | 2 | 1 to 2 | Trafo-2 | Power Transformer
1059 | UTILITY | HBI | 0.63 | 0.63 | 0 - 0.9 | BF-RWTP | Distribution Transformer
1060 | UTILITY | VARIAV-OLD | 2.5 | 2.5 | 3 to 5 | ESSAR | Power Transformer
1061 | UTILITY | VARIAV-OLD | 2.5 | 2.5 | 3 to 5 | RAMA | Power Transformer
1062 | UTILITY | VARIAV-OLD | 0.1 | 0.1 | 0 - 0.9 | LIGHTING | Distribution Transformer
1063 | UTILITY | VARIAV-NEW | 1 | 1 | 1 to 2 | ESSAR | Power Transformer
1064 | UTILITY | VARIAV-NEW | 1 | 1 | 1 to 2 | RAMA | Power Transformer
1065 | UTILITY | LPG JETTY | 1 | 1 | 1 to 2 | Trafo | Power Transformer
1066 | UTILITY | LCSS-3 | 2 | 2 | 1 to 2 | Trafo-1 | Power Transformer